## Timing Module (PTM1588)
Variable name | [14 empty] | In/Out In - from device Out - to device | Description | Hardware Allocation
Device
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Power |  |  |  |  | Out | Set the power state of the device | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Power_RBV |  |  |  |  | In | Get the power state of the device | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Reset |  |  |  |  | Out | Reset the device | 55GAD0-PCF-9002
State Machine
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | StateMachine | - | getState |  |  | In | Get device state (NDS State Machine) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | StateMachine | - | setState |  |  | Out | Set device state (NDS State Machine) | 55GAD0-PCF-9002
Firmware
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(FIRMWARE_NAME) | - | STM | - | getState | In | Get module state (NDS State Machine) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(FIRMWARE_NAME) | - | STM | - | setState | Out | Set module state (NDS State Machine) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(FIRMWARE_NAME) | - | HWRevision |  |  | In | Hardware revision ID | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(FIRMWARE_NAME) | - | SerialNumber |  |  | In | Device serial number | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(FIRMWARE_NAME) | - | Model |  |  | In | Device model | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(FIRMWARE_NAME) | - | Type |  |  | In | Device type | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(FIRMWARE_NAME) | - | DriverVersion |  |  | In | Driver version | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(FIRMWARE_NAME) | - | Status |  |  | In | Firmware status | 55GAD0-PCF-9002
Timing
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TIMING_NAME) | - | STM | - | getState | In | Get module state (NDS State Machine) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TIMING_NAME) | - | STM | - | setState | Out | Set module state (NDS State Machine) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TIMING_NAME) | - | SyncStatus |  |  | In | Synchronization Status | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TIMING_NAME) | - | SecsLastSync |  |  | In | Seconds since last synchronization | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TIMING_NAME) | - | Time |  |  | In | Retrieve Time. Format (sec, ns) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TIMING_NAME) | - | HTime |  |  | In | Retrieve Time. Format - UTC | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TIMING_NAME) | - | TimeSec |  |  | In | Seconds from Time PV | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TIMING_NAME) | - | TimeNano |  |  | In | Nanoseconds from Time PV | 55GAD0-PCF-9002
Terminal
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | STM | - | getGlobalState | In | Get module global state (NDS State Machine) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | STM | - | getState | In | Get module state (NDS State Machine) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | STM | - | setState | Out | Set module state (NDS State Machine) | 55GAD0-PCF-9002
Terminal - Timestamping
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | TS | - | Enable | Out | Enable/disable timestamping | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | TS | - | Enable_RBV | In | Timestamping status - enabled/disabled | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | TS | - | MaxTimestamps | In | Maximum number of timestamps | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | TS | - | Overflow | In | Get timestamps queue overflow status | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | TS | - | Timestamps | In | Get timestamp from queue | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | TS | - | TimestampsSec | In | Seconds from Timestamp PV | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | TS | - | TimestampsNano | In | Nanoseconds from Timestamp PV | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | TS | - | TimestampsID | In | ID from Timestamp PV | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | TS | - | TimestampsEdge | In | Edge from Timestamp PV | 55GAD0-PCF-9002
Terminal - FTE
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | ModeSet | Out | Mode of FTE to generate | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | StartTimeSet | Out | Start time of the FTE | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | StopTimeSet | Out | Stop time of the FTE | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | LevelSet | Out | Digital level of the FTE | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | PeriodNsecSet | Out | Period in nanoseconds for clock | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | DutyCycleSet | Out | Duty cycle of the clock in ns | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | Set | Out | Set the FTE using the parameters configured | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | SetStatus | In | Set FTE configuration success or error | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | SetCode | In | Code of success/error setting FTE configuration | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | StartTimeSuppress | Out | Start time on FTE suppression | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | ModeSuppress | Out | Mode of suppress FTE/clock | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | AllSuppress | Out | Suppress one or suppress all FTEs | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | Suppress | Out | Apply configured suppress | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | SuppressCode | In | Success/error on FTE suppression | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | SuppressStatus | In | Report on FTE suppression | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | TerminalChgPeriod | Out | Terminal to change the period of FTE | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | PeriodChgPeriod | Out | Period in nanoseconds to change on FTE | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | ChgPeriod | Out | Change the period | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | ChgPeriodStatus | Out | FTE clock period change | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | ChgPeriodCode | In | Success/error on FTE changing | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | TerminalPending | Out | Update pending value | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | PendingValue | In | Pending FTEs in the terminal | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | PendingStatus | In | Get pending FTEs | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | PendingCode | In | Success/error on getting pending FTEs | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(TERMINAL_NAME) | - | FTE | - | Maximum | In | Get maximum number of FTEs | 55GAD0-PCF-9002
Routing
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | STM | - | getState | In | Get module state (NDS State Machine) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | STM | - | setState | Out | Set module state (NDS State Machine) | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | ClkSrc |  |  | Out | Source clock | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | ClkDst |  |  | Out | Terminal where the clock will be connected | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | ClkSet |  |  | Out | Route the clock source to destination | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | ClkSetStatus |  |  | In | Clock routing set status message | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | ClkSetCode |  |  | In | Clock routing set status code | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | ClkDstRead |  |  | Out | Clock destination connection configuration read | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | ClkSrcRead |  |  | In | Clock source of selected clock destination | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermSrc |  |  | Out | Terminal source | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermDst |  |  | Out | Terminal destination | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermSyncSet |  |  | Out | Terminal sync mode set | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermInverSet |  |  | Out | Terminal inversion mode set | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermSet |  |  | Out | Terminal routing set | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermSetStatus |  |  | In | Terminal routing set status message | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermSetCode |  |  | In | Terminal routing set status code | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermDstRead |  |  | Out | Terminal destination connection configuration read | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermSrcRead |  |  | In | Terminal source of selected terminal destination | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermSyncRead |  |  | In | Terminal sync mode of selected terminal destination | 55GAD0-PCF-9002
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(ROUTING_NAME) | - | TermInvertRead |  |  | In | Terminal invert mode of selected terminal destination | 55GAD0-PCF-9002

## Timing Module (PTM1588)_S
$(CBS1) | D1
$(CBS2) | N9
$(BOARDTYPE) | NISYNCVIS
$(BOARDTYPEIDX) | 0
$(FIRMWARE_NAME) | FIRM
$(TIMING_NAME) | TIMING
$(TERMINAL_NAME) | TR0 | TR1 | TR2
$(ROUTING_NAME) | ROUTING

## Frame Grabber (UFG-10GE)
Variable name | [12 empty] | In/Out In - from device Out - to device | Description | Hardware Allocation
Acquisition Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionMode_RBV | In | Get Acquisition mode register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionMode | Out | Set Acquisition mode register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStart | Out | Set Start image acquisition register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStop | Out | Set Stop image acquisition register | 55GA00-PCF-0001
Device Information
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSerialNumber | In | Get device serial number | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceFirmwareVersion | In | Get device firmware version | 55GA00-PCF-0001
Image Format Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Height_RBV | In | Get Height register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Height | Out | Set Height register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Width_RBV | In | Get Width register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Width | Out | Set Width register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | PixelFormat_RBV | In | Get PixelFormat | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | PixelFormat | Out | Set PixelFormat | 55GA00-PCF-0001
Image Generator
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ImageGeneratorEnable_RBV | In | Get ImageGeneratorEnable register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ImageGeneratorEnable | Out | Set ImageGeneratorEnable register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImageWidth_RBV | In | Get GeneratedImageWidth register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImageWidth | Out | Set GeneratedImageWidth register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImageHeight_RBV | In | Get Height register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImageHeight | Out | Set Height register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImageFramerate_RBV | In | Get GeneratedImage Framerate register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImageFramerate | Out | Set GeneratedImage Framerate register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImagePattern_RBV | In | Get GeneratedImagePattern register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImagePattern | Out | Set GeneratedImagePattern register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImagePixelFormat_RBV | In | Get GeneratedImagePixelFormat register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GeneratedImagePixelFormat | Out | Set GeneratedImagePixelFormat register | 55GA00-PCF-0001
Transport Layer Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TLParamsLocked_RBV | In | Get Flag to indicate if features are locked during acquisition. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TLParamsLocked | Out | Set Flag to indicate if features are locked during acquisition. | 55GA00-PCF-0001
Triggering
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_TYPE_SELECT_RBV | In | Get EVENT_TYPE_SELECT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_TYPE_SELECT | Out | Set EVENT_TYPE_SELECT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_LINE_STATE_RBV | In | Get EVENT_LINE_STATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_LINE_STATE | Out | Set EVENT_LINE_STATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_LINE_OVERRIDE_RBV | In | Get EVENT_LINE_OVERRIDE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_LINE_OVERRIDE | Out | Set EVENT_LINE_OVERRIDE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_LINE_ENABLE_RBV | In | Get EVENT_LINE_ENABLE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_LINE_ENABLE | Out | Set EVENT_LINE_ENABLE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_LINE_SELECT_RBV | In | Get EVENT_LINE_SELECT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | EVENT_LINE_SELECT | Out | Set EVENT_LINE_SELECT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_STAMP_SELECT_RBV | In | Get TMG_STAMP_SELECT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_STAMP_SELECT | Out | Set TMG_STAMP_SELECT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHA_ENABLE_RBV | In | Get TMG_PHA_ENABLE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHA_ENABLE | Out | Set TMG_PHA_ENABLE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_ENABLE_RBV | In | Get TMG_TRG_ENABLE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_ENABLE | Out | Set TMG_TRG_ENABLE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TST_ENABLE_RBV | In | Get TMG_TST_ENABLE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TST_ENABLE | Out | Set TMG_TST_ENABLE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_LOST_RESET | Out | Set TMG_LOST_RESET Reg | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_FORCE | Out | Set TMG_TRG_FORCE Reg | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CLK_SRC_RBV | In | Get TMG_CLK_SRC register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CLK_SRC | Out | Set TMG_CLK_SRC register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TSINC_RBV | In | Get TMG_TSINC register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TSINC | Out | Set TMG_TSINC register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TS_RBV | In | Get TMG_TS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TS | Out | Set TMG_TS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PULSE_LEN_RBV | In | Get TMG_PULSE_LEN register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PULSE_LEN | Out | Set TMG_PULSE_LEN register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PERIOD_RBV | In | Get TMG_PERIOD register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PERIOD | Out | Set TMG_PERIOD register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_1_BYPASS_RBV | In | Get TMG_CC_1_BYPASS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_1_BYPASS | Out | Set TMG_CC_1_BYPASS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_1_INVERT_RBV | In | Get TMG_CC_1_INVERT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_1_INVERT | Out | Set TMG_CC_1_INVERT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_1_VALUE_RBV | In | Get TMG_CC_1_VALUE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_1_VALUE | Out | Set TMG_CC_1_VALUE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_1_MODE_RBV | In | Get TMG_CC_1_MODE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_1_MODE | Out | Set TMG_CC_1_MODE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_2_BYPASS_RBV | In | Get TMG_CC_2_BYPASS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_2_BYPASS | Out | Set TMG_CC_2_BYPASS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_2_INVERT_RBV | In | Get TMG_CC_2_INVERT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_2_INVERT | Out | Set TMG_CC_2_INVERT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_2_VALUE_RBV | In | Get TMG_CC_2_VALUE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_2_VALUE | Out | Set TMG_CC_2_VALUE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_2_MODE_RBV | In | Get TMG_CC_2_MODE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_2_MODE | Out | Set TMG_CC_2_MODE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_3_BYPASS_RBV | In | Get TMG_CC_3_BYPASS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_3_BYPASS | Out | Set TMG_CC_3_BYPASS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_3_INVERT_RBV | In | Get TMG_CC_3_INVERT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_3_INVERT | Out | Set TMG_CC_3_INVERT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_3_VALUE_RBV | In | Get TMG_CC_3_VALUE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_3_VALUE | Out | Set TMG_CC_3_VALUE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_3_MODE_RBV | In | Get TMG_CC_3_MODE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_3_MODE | Out | Set TMG_CC_3_MODE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_4_BYPASS_RBV | In | Get TMG_CC_4_BYPASS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_4_BYPASS | Out | Set TMG_CC_4_BYPASS register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_4_INVERT_RBV | In | Get TMG_CC_3_INVERT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_4_INVERT | Out | Set TMG_CC_3_INVERT register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_4_VALUE_RBV | In | Get TMG_CC_4_VALUE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_4_VALUE | Out | Set TMG_CC_4_VALUE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_4_MODE_RBV | In | Get TMG_CC_3_MODE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_CC_4_MODE | Out | Set TMG_CC_3_MODE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_STP_NOW | Out | Set TMG_STP_NOW Reg | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_STP_EDGE_RBV | In | Get TMG_STP_EDGE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_STP_EDGE | Out | Set TMG_STP_EDGE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_STP_GATE_RBV | In | Get TMG_STP_GATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_STP_GATE | Out | Set TMG_STP_GATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_STP_LINE_RBV | In | Get TMG_STP_LINE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_STP_LINE | Out | Set TMG_STP_LINE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TST_NOW | Out | Set TMG_TST_NOW Reg | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TST_EDGE_RBV | In | Get TMG_TST_EDGE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TST_EDGE | Out | Set TMG_TST_EDGE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TST_GATE_RBV | In | Get TMG_TST_GATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TST_GATE | Out | Set TMG_TST_GATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TST_LINE_RBV | In | Get TMG_TST_LINE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TST_LINE | Out | Set TMG_TST_LINE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_NOW | Out | Set TMG_TRG_NOW Reg | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_EDGE_RBV | In | Get TMG_TRG_EDGE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_EDGE | Out | Set TMG_TRG_EDGE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_GATE_RBV | In | Get TMG_TRG_GATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_GATE | Out | Set TMG_TRG_GATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_LINE_RBV | In | Get TMG_TRG_LINE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TRG_LINE | Out | Set TMG_TRG_LINE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHA_NOW | Out | Set TMG_PHA_NOW Reg | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHA_EDGE_RBV | In | Get TMG_PHA_EDGE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHA_EDGE | Out | Set TMG_PHA_EDGE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHA_GATE_RBV | In | Get TMG_PHA_GATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHA_GATE | Out | Set TMG_PHA_GATE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHA_LINE_RBV | In | Get TMG_PHA_LINE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHA_LINE | Out | Set TMG_PHA_LINE register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_TSCAP | In | Get TMG_TSCAP register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_LOST1 | In | Get TMG_LOST1 register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_LOST2 | In | Get TMG_LOST2 register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_FREQ | In | Get TMG_FREQ register | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TMG_PHASE | In | Get TMG_PHASE register | 55GA00-PCF-0001
Versioning
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GitShortCommitSHA | In | Get Git shortened commit hash | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GitCommitSHA | In | Get Git commit hash | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GitIsClean | In | Get Indicates if commit is clean | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GitTag | In | Get Git Tag | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GitBranch | In | Get Git Branch | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GitDate | In | Get current Git commit Date | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | VersionMajor | In | Get 1st version digit | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | VersionMinor | In | Get 2nd version digit | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | VersionPatch | In | Get 3rd version digit | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | VersionTweak | In | Get 4th version digit | 55GA00-PCF-0001

## Frame Grabber (UFG-10GE)_S
$(CBS1) | D1
$(CBS2) | N9
$(FGIDX) | 0 | 1
$(CAMIDX) | 0

## Camera (Infratec ImageIR10300)
Variable name | [14 empty] | In/Out In - from device Out - to device | Description | Hardware Allocation
Device
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ErrorSev |  |  |  |  | In | Get error severity | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ErrorSrc |  |  |  |  | In | Get error source | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ErrorMsg |  |  |  |  | In | Get error message | 55GAD0-PCF-9004
State Machine
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | StateMachine | - | GetState |  |  | In | Get device state (NDS State Machine) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | StateMachine | - | Cooling | - | GetState | In | Get cooling device state (NDS State Machine) | 55GAD0-PCF-9004
HR IR Camera
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | SerialNumber |  |  |  |  | In | Read serial number | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | FirmwareVersion |  |  |  |  | In | Read firmare version | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | IntegrationTime | - | Get |  |  | In | Read Integration Times | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | IntegrationTime | - | Set |  |  | Out | Write Integration Times | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | IntegrationTime | - | Number | - | Get | In | Read the number of Integration Times | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | IntegrationTime | - | Number |  | Set | Out | Write the number of Integration Times | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | InternalShutter | - | GetState |  |  | In | Read internal shutter state (open / close) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | InternalShutter | - | SetState |  |  | Out | Write internal shutter state (open / close) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Acquisition | - | Start |  |  | Out | Start Acquisition | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Acquisition | - | Stop |  |  | Out | Stop Acquisition | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Image |  |  |  |  | In | Get image | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Format | - | Get |  |  | In | Read format (full frame/ROI) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Format | - | Set |  |  | Out | Write format (full frame/ROI) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | PX | - | Get | In | Read the X coordinate of the ROI bottom left point. | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | PX | - | Set | Out | Write the X coordinate of the ROI bottom left point. | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | PY | - | Get | In | Read the Y coordinate of the ROI bottom left point. | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | PY | - | Set | Out | Write the Y coordinate of the ROI bottom left point. | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | Width | - | Get | In | Read the ROI width | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | Width | - | Set | Out | Write the ROI width | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | Height | - | Get | In | Read the ROI height | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | Height | - | Set | Out | Write the ROI height | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | GetState |  |  |  |  | In | Get state (on/off) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | SetState |  |  |  |  | Out | Set state (on/off) | 55GAD0-PCF-9004
Health monitoring
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | HEMON | - | Temperature |  |  | In | Read device temperature | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | HEMON | - | PowerCycleNb |  |  | In | Read the number of performed power cycles | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | HEMON | - | Hours |  |  | In | Read the number of performed operational hours | 55GAD0-PCF-9004

## Camera (Infratec ImageIR10300_S
$(CBS1) | D1
$(CBS2) | N9
$(BOARDTYPE) | HRIR
$(BOARDTYPEIDX) | 0

## Camera (Infratec ImageIR8300)
Variable name | [14 empty] | In/Out In - from device Out - to device | Description | Hardware Allocation
Device
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ErrorSev |  |  |  |  | In | Get error severity | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ErrorSrc |  |  |  |  | In | Get error source | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ErrorMsg |  |  |  |  | In | Get error message | 55GAD0-PCF-9004
State Machine
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | StateMachine | - | GetState |  |  | In | Get device state (NDS State Machine) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | StateMachine | - | Cooling | - | GetState | In | Get cooling device state (NDS State Machine) | 55GAD0-PCF-9004
HR IR Camera
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | SerialNumber |  |  |  |  | In | Read serial number | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | FirmwareVersion |  |  |  |  | In | Read firmare version | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | IntegrationTime | - | Get |  |  | In | Read Integration Times | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | IntegrationTime | - | Set |  |  | Out | Write Integration Times | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | IntegrationTime | - | Number | - | Get | In | Read the number of Integration Times | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | IntegrationTime | - | Number |  | Set | Out | Write the number of Integration Times | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | InternalShutter | - | GetState |  |  | In | Read internal shutter state (open / close) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | InternalShutter | - | SetState |  |  | Out | Write internal shutter state (open / close) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Acquisition | - | Start |  |  | Out | Start Acquisition | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Acquisition | - | Stop |  |  | Out | Stop Acquisition | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Image |  |  |  |  | In | Get image | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Format | - | Get |  |  | In | Read format (full frame/ROI) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | Format | - | Set |  |  | Out | Write format (full frame/ROI) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | PX | - | Get | In | Read the X coordinate of the ROI bottom left point. | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | PX | - | Set | Out | Write the X coordinate of the ROI bottom left point. | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | PY | - | Get | In | Read the Y coordinate of the ROI bottom left point. | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | PY | - | Set | Out | Write the Y coordinate of the ROI bottom left point. | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | Width | - | Get | In | Read the ROI width | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | Width | - | Set | Out | Write the ROI width | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | Height | - | Get | In | Read the ROI height | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ROI | - | Height | - | Set | Out | Write the ROI height | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | GetState |  |  |  |  | In | Get state (on/off) | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | SetState |  |  |  |  | Out | Set state (on/off) | 55GAD0-PCF-9004
Health monitoring
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | HEMON | - | Temperature |  |  | In | Read device temperature | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | HEMON | - | PowerCycleNb |  |  | In | Read the number of performed power cycles | 55GAD0-PCF-9004
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | HEMON | - | Hours |  |  | In | Read the number of performed operational hours | 55GAD0-PCF-9004

## Camera (Infratec ImageIR8300)_S
$(CBS1) | D1
$(CBS2) | N9
$(BOARDTYPE) | HSIR
$(BOARDTYPEIDX) | 0

## Camera (Baumer VQXG-120M)
Variable name | [12 empty] | In/Out In - from device Out - to device | Description | Hardware Allocation
Acquisition Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionMode_RBV | In | Get the acquisition mode of the device. It defines mainly the number of frames to capture during an acquisition and the way the acquisition stops. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionMode | Out | Set the acquisition mode of the device. It defines mainly the number of frames to capture during an acquisition and the way the acquisition stops. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStart | Out | Start the Acquisition of the device. The number of frames captured is specified by AcquisitionMode. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStop | Out | Stop the Acquisition of the device at the end of the current Frame. It is mainly used when AcquisitionMode is Continuous but can be used in any acquisition mode. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionAbort | Out | Abort the Acquisition immediately. This will end the capture without completing the current Frame or waiting on a trigger. If no Acquisition is in progress, the command is ignored. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionFrameRate_RBV | In | Get the acquisition rate (in Hertz) at which the frames are captured. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionFrameRate | Out | Set the acquisition rate (in Hertz) at which the frames are captured. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionFrameRateLimit | In | Get the maximal acquisition rate (in Hertz) at which the frames are captured. This is the maximum frequenz to give trigger at the device | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStatusSelector_RBV | In | Get the internal acquisition signal to read using AcquisitionStatus. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStatusSelector | Out | Select the internal acquisition signal to read using AcquisitionStatus. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStatus | In | Read the state of the internal acquisition signal selected using AcquisitionStatusSelector. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerSelector | Out | Select the type of trigger to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerMode | Out | Controls if the selected trigger is active. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerSoftware | Out | Generate an internal trigger. TriggerSource must be set to Software. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerSource_RBV | In | Get the internal signal or physical input Line to use as the trigger source. The selected trigger must have its TriggerMode set to On. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerSource | Out | Set the internal signal or physical input Line to use as the trigger source. The selected trigger must have its TriggerMode set to On. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerActivation_RBV | In | Get the activation mode of the trigger. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerActivation | Out | Set the activation mode of the trigger. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerOverlap_RBV | In | Get the type trigger overlap permitted with the previous frame. This defines when a valid trigger will be accepted (or latched) for a new frame. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerOverlap | Out | Set the type trigger overlap permitted with the previous frame. This defines when a valid trigger will be accepted (or latched) for a new frame. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerDelay_RBV | In | Get the delay in microseconds (us) to apply after the trigger reception before activating it. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerDelay | Out | Set the delay in microseconds (us) to apply after the trigger reception before activating it. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureMode_RBV | In | Get the operation mode of the Exposure (or shutter). | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureMode | Out | Set the operation mode of the Exposure (or shutter). | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureTime_RBV | In | Get the Exposure time when ExposureMode is Timed and ExposureAuto is Off. This controls the duration where the photosensitive cells are exposed to light. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureTime | Out | Set the Exposure time when ExposureMode is Timed and ExposureAuto is Off. This controls the duration where the photosensitive cells are exposed to light. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionFrameRateEnable | Out | Enable the acquisition at the framerate specified by AcquisitionFrameRate. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReadoutMode_RBV | In | Get the operation mode of the readout for the acquisition. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReadoutMode | Out | Set the operation mode of the readout for the acquisition. | 55GA00-PCF-0001
Analog Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GainSelector_RBV | In | Read which Gain is controlled by the various Gain features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GainSelector | Out | Select which Gain is controlled by the various Gain features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Gain_RBV | In | Read the selected gain as an absolute physical value. This is an amplification factor applied to the video signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Gain | Out | Control the selected gain as an absolute physical value. This is an amplification factor applied to the video signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackLevelSelector_RBV | In | Read which Black Level is controlled by the various Black Level features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackLevelSelector | Out | Select which Black Level is controlled by the various Black Level features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BalanceWhiteAuto_RBV | In | Read the mode for automatic white balancing between the color channels. The white balancing ratios are automatically adjusted. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BalanceWhiteAuto | Out | Control the mode for automatic white balancing between the color channels. The white balancing ratios are automatically adjusted. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackLevel_RBV | In | Read the analog black level as an absolute physical value. This represents a DC offset applied to the video signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackLevel | Out | Control the analog black level as an absolute physical value. This represents a DC offset applied to the video signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackReferenceCorrectionEnable_RBV | In | Check if the black reference correction of the sensor is activated. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackReferenceCorrectionEnable | Out | Activate the black reference correction of the sensor. | 55GA00-PCF-0001
Counter And Timer Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterSelector_RBV | In | Get which Counter is selected to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterSelector | Out | Select which Counter to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterEventSource_RBV | In | Get the events that will be the source to increment the Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterEventSource | Out | Select the events that will be the source to increment the Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterEventActivation_RBV | In | Get the Activation mode Event Source signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterEventActivation | Out | Select the Activation mode Event Source signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterResetSource_RBV | In | Get the signals that will be the source to reset the Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterResetSource | Out | Select the signals that will be the source to reset the Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterResetActivation_RBV | In | Get the Activation mode of the Counter Reset Source signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterResetActivation | Out | Select the Activation mode of the Counter Reset Source signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterReset | Out | Execute a software reset of the selected Counter and starts it. The counter starts counting events immediately after the reset unless a Counter trigger is active. CounterReset can be used to reset the Counter independently from the CounterResetSource. To disable the counter temporarily, set CounterEventSource to Off. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterValue_RBV | In | Read the current value of the selected Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterValue | Out | Write the current value of the selected Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterValueAtReset | In | Read the value of the selected Counter when it was reset by a trigger or by an explicit CounterReset command. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterDuration_RBV | In | Read the duration (or number of events) before the CounterEnd event is generated. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterDuration | Out | Set the duration (or number of events) before the CounterEnd event is generated. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerSelector_RBV | In | Get the Timer selected to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerSelector | Out | Select which Timer to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerDuration_RBV | In | Get the duration (in microseconds) of the Timer pulse. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerDuration | Out | Set the duration (in microseconds) of the Timer pulse. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerDelay_RBV | In | Get the duration (in microseconds) of the delay to apply at the reception of a trigger before starting the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerDelay | Out | Set the duration (in microseconds) of the delay to apply at the reception of a trigger before starting the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerTriggerSource_RBV | In | Get the source of the trigger to start the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerTriggerSource | Out | Set the source of the trigger to start the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerTriggerActivation_RBV | In | Get the activation mode of the trigger to start the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerTriggerActivation | Out | Set the activation mode of the trigger to start the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | FrameCounter_RBV | In | Get the frame counter, which is part of the chunk data too. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | FrameCounter | Out | Set the frame counter, which is part of the chunk data too. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerCounterLatchValue | In | Get the latched value of the trigger counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerCounterLatch | Out | Latche the current timestamp counter into TimestampLatchValue. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerCounterReset | Out | Reset the current value of the device trigger counter. | 55GA00-PCF-0001
Device Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceVendorName | In | Get name of the manufacturer of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceModelName | In | Get model of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceUserID_RBV | In | Get user-programmable device identifier. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceUserID | Out | Set user-programmable device identifier. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSerialNumber | In | Get device`s serial number. This string is a unique identifier of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceManufacturerInfo | In | Get manufacturer information about the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceVersion | In | Get version of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceFirmwareVersion | In | Get version of the firmware in the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceFamilyName | In | Get identifier of the product family of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSFNCVersionMajor | In | Get major version of the Standard Features Naming Convention that was used to create the device`s GenICam XML. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSFNCVersionMinor | In | Get minor version of the Standard Features Naming Convention that was used to create the device`s GenICam XML. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSFNCVersionSubMinor | In | Get sub minor version of Standard Features Naming Convention that was used to create the device`s GenICam XML. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceReset | Out | Reset the device to its power up state. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceResetToDeliveryState | Out | Reset the device to its delivery state including the IP settings. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureSelector_RBV | In | Get the selected location within the device, where the temperature will be measured. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureSelector | Out | Select the location within the device, where the temperature will be measured. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatus | In | Get the current temperature status of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureExceeded | In | Check if the device operates in critical temperature range. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatusTransitionSelector_RBV | In | Get which temperature transition is controlled by the DeviceTemperatureStatusTransition feature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatusTransitionSelector | Out | Select which temperature transition is controlled by the DeviceTemperatureStatusTransition feature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatusTransition_RBV | In | Get temperature threshold for selected status transition in degrees Celsius (C). | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatusTransition | Out | Set temperature threshold for selected status transition in degrees Celsius (C). | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceScanType | In | Get scan type of the sensor of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSensorType | In | Get the type of the sensor. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTLType | In | Get Transport Layer type of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTLVersionMajor | In | Get Major version of the Transport Layer of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTLVersionMinor | In | Get Minor version of the Transport Layer of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTLVersionSubMinor | In | Get Sub minor version of the Transport Layer of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceRegistersEndianness | In | Get endianess of the register of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceCharacterSet | In | Get character set used by the strings of the device`s bootstrap registers. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceType | In | Get the device type. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkSelector | Out | Select which Link of the device to control. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkSpeed | In | Get the speed of transmission negotiated on the specified Link. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkHeartbeatMode | Out | Activate or deactivate the Link`s heartbeat. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkHeartbeatTimeout | Out | Control the current heartbeat timeout of the specific Link. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkCommandTimeout | In | Get the current command timeout of the specific Link. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelCount | In | Get the number of streaming channels supported by the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceEventChannelCount | In | Get the number of event channels supported by the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelSelector | Out | Select the stream channel to control. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelType | In | Get the type of the stream channel. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelEndianness_RBV | In | Get endianess of multi-byte pixel data for this stream. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelEndianness | Out | Set endianess of multi-byte pixel data for this stream. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelPacketSize_RBV | In | Get the stream packet size, in bytes, to send on the selected channel for a Transmitter or specifies the maximum packet size supported by a receiver. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelPacketSize | Out | Set the stream packet size, in bytes, to send on the selected channel for a Transmitter or specifies the maximum packet size supported by a receiver. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReadOutTime | In | Get time in us for current format settings. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimestampLatch | Out | Latch the current timestamp counter into TimestampLatchValue. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimestampReset | Out | Reset the current value of the device timestamp counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimestampLatchValue | In | Get the latched value of the timestamp counter. | 55GA00-PCF-0001
Digital IO Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineSelector | Out | Select the physical line (or pin) of the external device connector to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineMode | Out | Control if the physical Line is used to Input or Output a signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineInverter | Out | Control the inversion of the signal of the selected input or output Line. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineStatus | In | Return the current status of the selected input or output Line. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineSource | Out | Select which internal acquisition or I/O source signal to output on the selected Line. LineMode must be Output. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputSelector | Out | Select which bit of the User Output register will be set by UserOutputValue. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputValue_RBV | In | Get the value of the bit selected by UserOutputSelector. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputValue | Out | Set the value of the bit selected by UserOutputSelector. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputValueAll_RBV | In | Get the value of all the bits of the User Output register. It is subject to the UserOutputValueAllMask. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputValueAll | Out | Set the value of all the bits of the User Output register. It is subject to the UserOutputValueAllMask. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineDebouncerHighTimeAbs_RBV | In | Get the absolute value of the selected line debouncer time in microseconds for switch from low to high. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineDebouncerHighTimeAbs | Out | Set the absolute value of the selected line debouncer time in microseconds for switch from low to high. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineDebouncerLowTimeAbs_RBV | In | Get the absolute value of the selected line debouncer time in microseconds for switch from high to low. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineDebouncerLowTimeAbs | Out | Set the absolute value of the selected line debouncer time in microseconds for switch from high to low. | 55GA00-PCF-0001
Image Format Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | SensorWidth | In | Get effective width of the sensor in pixels. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | SensorHeight | In | Get effective height of the sensor in pixels. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | WidthMax | In | Get maximum width of the image (in pixels). The dimension is calculated after horizontal binning, decimation or any other function changing the horizontal dimension of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | HeightMax | In | Get maximum height of the image (in pixels). This dimension is calculated after vertical binning, decimation or any other function changing the vertical dimension of the image | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningSelector_RBV | In | Read which binning engine is controlled by the BinningHorizontal and BinningVertical features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningSelector | Out | Select which binning engine is controlled by the BinningHorizontal and BinningVertical features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningHorizontal_RBV | In | Get number of horizontal photo-sensitive cells to combine together. This increases the intensity (or signal to noise ratio) of the pixels and reduces the horizontal resolution (width) of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningHorizontal | Out | Set number of horizontal photo-sensitive cells to combine together. This increases the intensity (or signal to noise ratio) of the pixels and reduces the horizontal resolution (width) of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningHorizontalMode_RBV | In | Get the mode to use to combine horizontal photo-sensitive cells together when BinningHorizontal is used. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningHorizontalMode | Out | Set the mode to use to combine horizontal photo-sensitive cells together when BinningHorizontal is used. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningVertical_RBV | In | Get number of vertical photo-sensitive cells to combine together. This increases the intensity (or signal to noise ratio) of the pixels and reduces the vertical resolution (height) of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningVertical | Out | Set number of vertical photo-sensitive cells to combine together. This increases the intensity (or signal to noise ratio) of the pixels and reduces the vertical resolution (height) of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningVerticalMode_RBV | In | Get the mode used to combine horizontal photo-sensitive cells together when BinningVertical is used. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningVerticalMode | Out | Set the mode used to combine horizontal photo-sensitive cells together when BinningVertical is used. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReverseX | Out | Flip horizontally the image sent by the device. The Region of interest is applied after the flipping. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReverseY | Out | Flip vertically the image sent by the device. The Region of interest is applied after the flipping. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TestPatternGeneratorSelector_RBV | In | Get which test pattern generator is controlled by the TestPattern feature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TestPatternGeneratorSelector | Out | Set which test pattern generator is controlled by the TestPattern feature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TestPattern_RBV | In | Get the type of test pattern that is generated by the device as image source. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TestPattern | Out | Set the type of test pattern that is generated by the device as image source. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperature | In | Get Device Temperature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Width_RBV | In | Get width. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Width | Out | Set width. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Height_RBV | In | Get height. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Height | Out | Set height. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | OffsetX_RBV | In | Get offset X. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | OffsetX | Out | Set offset X. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | OffsetY_RBV | In | Get offset Y. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | OffsetY | Out | Set offset Y. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | PixelFormat_RBV | In | Get pixel Format. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | PixelFormat | Out | Set pixel Format. | 55GA00-PCF-0001
Shutter Line Correction
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineCorrectionEnable | Out | Enable the shutterline correction. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineOffsetEven_RBV | In | Get value of Shutterline Offset Even. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineOffsetEven | Out | Set value of Shutterline Offset Even. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureLinesOffsetEven_RBV | In | Get value of Exposure Lines Offset Even. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureLinesOffsetEven | Out | Set value of Exposure Lines Offset Even. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineOffsetOdd_RBV | In | Get value of Shutterline Offset Odd. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineOffsetOdd | Out | Set value of Shutterline Offset Odd. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureLinesOffsetOdd_RBV | In | Get value of Exposure Lines Offset Odd. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureLinesOffsetOdd | Out | Set value of Exposure Lines Offset Odd. | 55GA00-PCF-0001
Transport Layer Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | PayloadSize | In | Get the number of bytes transferred for each image or chunk on the stream channel. This includes any end-of-line, end-of-frame statistics or other stamp data. This is the total size of data payload for a data block. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TLParamsLocked | In | Check if the Transport Layer is locked to prevent critical features changes during acquisition. | 55GA00-PCF-0001

## Camera (Baumer VQXG-120M)_S
$(CBS1) | D1
$(CBS2) | N9
$(FGIDX) | 0
$(CAMIDX) | 0

## Camera (Baumer VLXT-17M)
Variable name | [12 empty] | In/Out In - from device Out - to device | Description | Hardware Allocation
Acquisition Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionMode_RBV | In | Get the acquisition mode of the device. It defines mainly the number of frames to capture during an acquisition and the way the acquisition stops. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionMode | Out | Set the acquisition mode of the device. It defines mainly the number of frames to capture during an acquisition and the way the acquisition stops. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStart | Out | Start the Acquisition of the device. The number of frames captured is specified by AcquisitionMode. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStop | Out | Stop the Acquisition of the device at the end of the current Frame. It is mainly used when AcquisitionMode is Continuous but can be used in any acquisition mode. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionAbort | Out | Abort the Acquisition immediately. This will end the capture without completing the current Frame or waiting on a trigger. If no Acquisition is in progress, the command is ignored. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionFrameRate_RBV | In | Get the acquisition rate (in Hertz) at which the frames are captured. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionFrameRate | Out | Set the acquisition rate (in Hertz) at which the frames are captured. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionFrameRateLimit | In | Get the maximal acquisition rate (in Hertz) at which the frames are captured. This is the maximum frequenz to give trigger at the device | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStatusSelector_RBV | In | Get the internal acquisition signal to read using AcquisitionStatus. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStatusSelector | Out | Select the internal acquisition signal to read using AcquisitionStatus. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionStatus | In | Read the state of the internal acquisition signal selected using AcquisitionStatusSelector. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerSelector | Out | Select the type of trigger to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerMode | Out | Controls if the selected trigger is active. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerSoftware | Out | Generate an internal trigger. TriggerSource must be set to Software. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerSource_RBV | In | Get the internal signal or physical input Line to use as the trigger source. The selected trigger must have its TriggerMode set to On. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerSource | Out | Set the internal signal or physical input Line to use as the trigger source. The selected trigger must have its TriggerMode set to On. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerActivation_RBV | In | Get the activation mode of the trigger. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerActivation | Out | Set the activation mode of the trigger. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerOverlap_RBV | In | Get the type trigger overlap permitted with the previous frame. This defines when a valid trigger will be accepted (or latched) for a new frame. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerOverlap | Out | Set the type trigger overlap permitted with the previous frame. This defines when a valid trigger will be accepted (or latched) for a new frame. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerDelay_RBV | In | Get the delay in microseconds (us) to apply after the trigger reception before activating it. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerDelay | Out | Set the delay in microseconds (us) to apply after the trigger reception before activating it. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureMode_RBV | In | Get the operation mode of the Exposure (or shutter). | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureMode | Out | Set the operation mode of the Exposure (or shutter). | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureTime_RBV | In | Get the Exposure time when ExposureMode is Timed and ExposureAuto is Off. This controls the duration where the photosensitive cells are exposed to light. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureTime | Out | Set the Exposure time when ExposureMode is Timed and ExposureAuto is Off. This controls the duration where the photosensitive cells are exposed to light. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | AcquisitionFrameRateEnable | Out | Enable the acquisition at the framerate specified by AcquisitionFrameRate. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReadoutMode_RBV | In | Get the operation mode of the readout for the acquisition. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReadoutMode | Out | Set the operation mode of the readout for the acquisition. | 55GA00-PCF-0001
Analog Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GainSelector_RBV | In | Read which Gain is controlled by the various Gain features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | GainSelector | Out | Select which Gain is controlled by the various Gain features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Gain_RBV | In | Read the selected gain as an absolute physical value. This is an amplification factor applied to the video signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Gain | Out | Control the selected gain as an absolute physical value. This is an amplification factor applied to the video signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackLevelSelector_RBV | In | Read which Black Level is controlled by the various Black Level features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackLevelSelector | Out | Select which Black Level is controlled by the various Black Level features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BalanceWhiteAuto_RBV | In | Read the mode for automatic white balancing between the color channels. The white balancing ratios are automatically adjusted. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BalanceWhiteAuto | Out | Control the mode for automatic white balancing between the color channels. The white balancing ratios are automatically adjusted. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackLevel_RBV | In | Read the analog black level as an absolute physical value. This represents a DC offset applied to the video signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackLevel | Out | Control the analog black level as an absolute physical value. This represents a DC offset applied to the video signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackReferenceCorrectionEnable_RBV | In | Check if the black reference correction of the sensor is activated. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BlackReferenceCorrectionEnable | Out | Activate the black reference correction of the sensor. | 55GA00-PCF-0001
Counter And Timer Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterSelector_RBV | In | Get which Counter is selected to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterSelector | Out | Select which Counter to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterEventSource_RBV | In | Get the events that will be the source to increment the Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterEventSource | Out | Select the events that will be the source to increment the Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterEventActivation_RBV | In | Get the Activation mode Event Source signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterEventActivation | Out | Select the Activation mode Event Source signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterResetSource_RBV | In | Get the signals that will be the source to reset the Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterResetSource | Out | Select the signals that will be the source to reset the Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterResetActivation_RBV | In | Get the Activation mode of the Counter Reset Source signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterResetActivation | Out | Select the Activation mode of the Counter Reset Source signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterReset | Out | Execute a software reset of the selected Counter and starts it. The counter starts counting events immediately after the reset unless a Counter trigger is active. CounterReset can be used to reset the Counter independently from the CounterResetSource. To disable the counter temporarily, set CounterEventSource to Off. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterValue_RBV | In | Read the current value of the selected Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterValue | Out | Write the current value of the selected Counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterValueAtReset | In | Read the value of the selected Counter when it was reset by a trigger or by an explicit CounterReset command. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterDuration_RBV | In | Read the duration (or number of events) before the CounterEnd event is generated. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | CounterDuration | Out | Set the duration (or number of events) before the CounterEnd event is generated. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerSelector_RBV | In | Get the Timer selected to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerSelector | Out | Select which Timer to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerDuration_RBV | In | Get the duration (in microseconds) of the Timer pulse. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerDuration | Out | Set the duration (in microseconds) of the Timer pulse. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerDelay_RBV | In | Get the duration (in microseconds) of the delay to apply at the reception of a trigger before starting the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerDelay | Out | Set the duration (in microseconds) of the delay to apply at the reception of a trigger before starting the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerTriggerSource_RBV | In | Get the source of the trigger to start the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerTriggerSource | Out | Set the source of the trigger to start the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerTriggerActivation_RBV | In | Get the activation mode of the trigger to start the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimerTriggerActivation | Out | Set the activation mode of the trigger to start the Timer. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | FrameCounter_RBV | In | Get the frame counter, which is part of the chunk data too. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | FrameCounter | Out | Set the frame counter, which is part of the chunk data too. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerCounterLatchValue | In | Get the latched value of the trigger counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerCounterLatch | Out | Latche the current timestamp counter into TimestampLatchValue. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TriggerCounterReset | Out | Reset the current value of the device trigger counter. | 55GA00-PCF-0001
Device Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceVendorName | In | Get name of the manufacturer of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceModelName | In | Get model of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceUserID_RBV | In | Get user-programmable device identifier. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceUserID | Out | Set user-programmable device identifier. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSerialNumber | In | Get device`s serial number. This string is a unique identifier of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceManufacturerInfo | In | Get manufacturer information about the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceVersion | In | Get version of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceFirmwareVersion | In | Get version of the firmware in the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceFamilyName | In | Get identifier of the product family of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSFNCVersionMajor | In | Get major version of the Standard Features Naming Convention that was used to create the device`s GenICam XML. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSFNCVersionMinor | In | Get minor version of the Standard Features Naming Convention that was used to create the device`s GenICam XML. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSFNCVersionSubMinor | In | Get sub minor version of Standard Features Naming Convention that was used to create the device`s GenICam XML. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceReset | Out | Reset the device to its power up state. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceResetToDeliveryState | Out | Reset the device to its delivery state including the IP settings. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureSelector_RBV | In | Get the selected location within the device, where the temperature will be measured. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureSelector | Out | Select the location within the device, where the temperature will be measured. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatus | In | Get the current temperature status of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureExceeded | In | Check if the device operates in critical temperature range. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatusTransitionSelector_RBV | In | Get which temperature transition is controlled by the DeviceTemperatureStatusTransition feature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatusTransitionSelector | Out | Select which temperature transition is controlled by the DeviceTemperatureStatusTransition feature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatusTransition_RBV | In | Get temperature threshold for selected status transition in degrees Celsius (C). | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperatureStatusTransition | Out | Set temperature threshold for selected status transition in degrees Celsius (C). | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceScanType | In | Get scan type of the sensor of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceSensorType | In | Get the type of the sensor. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTLType | In | Get Transport Layer type of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTLVersionMajor | In | Get Major version of the Transport Layer of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTLVersionMinor | In | Get Minor version of the Transport Layer of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTLVersionSubMinor | In | Get Sub minor version of the Transport Layer of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceRegistersEndianness | In | Get endianess of the register of the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceCharacterSet | In | Get character set used by the strings of the device`s bootstrap registers. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceType | In | Get the device type. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkSelector | Out | Select which Link of the device to control. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkSpeed | In | Get the speed of transmission negotiated on the specified Link. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkHeartbeatMode | Out | Activate or deactivate the Link`s heartbeat. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkHeartbeatTimeout | Out | Control the current heartbeat timeout of the specific Link. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceLinkCommandTimeout | In | Get the current command timeout of the specific Link. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelCount | In | Get the number of streaming channels supported by the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceEventChannelCount | In | Get the number of event channels supported by the device. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelSelector | Out | Select the stream channel to control. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelType | In | Get the type of the stream channel. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelEndianness_RBV | In | Get endianess of multi-byte pixel data for this stream. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelEndianness | Out | Set endianess of multi-byte pixel data for this stream. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelPacketSize_RBV | In | Get the stream packet size, in bytes, to send on the selected channel for a Transmitter or specifies the maximum packet size supported by a receiver. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceStreamChannelPacketSize | Out | Set the stream packet size, in bytes, to send on the selected channel for a Transmitter or specifies the maximum packet size supported by a receiver. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReadOutTime | In | Get time in us for current format settings. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimestampLatch | Out | Latch the current timestamp counter into TimestampLatchValue. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimestampReset | Out | Reset the current value of the device timestamp counter. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TimestampLatchValue | In | Get the latched value of the timestamp counter. | 55GA00-PCF-0001
Digital IO Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineSelector | Out | Select the physical line (or pin) of the external device connector to configure. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineMode | Out | Control if the physical Line is used to Input or Output a signal. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineInverter | Out | Control the inversion of the signal of the selected input or output Line. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineStatus | In | Return the current status of the selected input or output Line. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineSource | Out | Select which internal acquisition or I/O source signal to output on the selected Line. LineMode must be Output. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputSelector | Out | Select which bit of the User Output register will be set by UserOutputValue. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputValue_RBV | In | Get the value of the bit selected by UserOutputSelector. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputValue | Out | Set the value of the bit selected by UserOutputSelector. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputValueAll_RBV | In | Get the value of all the bits of the User Output register. It is subject to the UserOutputValueAllMask. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | UserOutputValueAll | Out | Set the value of all the bits of the User Output register. It is subject to the UserOutputValueAllMask. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineDebouncerHighTimeAbs_RBV | In | Get the absolute value of the selected line debouncer time in microseconds for switch from low to high. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineDebouncerHighTimeAbs | Out | Set the absolute value of the selected line debouncer time in microseconds for switch from low to high. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineDebouncerLowTimeAbs_RBV | In | Get the absolute value of the selected line debouncer time in microseconds for switch from high to low. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | LineDebouncerLowTimeAbs | Out | Set the absolute value of the selected line debouncer time in microseconds for switch from high to low. | 55GA00-PCF-0001
Image Format Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | SensorWidth | In | Get effective width of the sensor in pixels. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | SensorHeight | In | Get effective height of the sensor in pixels. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | WidthMax | In | Get maximum width of the image (in pixels). The dimension is calculated after horizontal binning, decimation or any other function changing the horizontal dimension of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | HeightMax | In | Get maximum height of the image (in pixels). This dimension is calculated after vertical binning, decimation or any other function changing the vertical dimension of the image | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningSelector_RBV | In | Read which binning engine is controlled by the BinningHorizontal and BinningVertical features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningSelector | Out | Select which binning engine is controlled by the BinningHorizontal and BinningVertical features. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningHorizontal_RBV | In | Get number of horizontal photo-sensitive cells to combine together. This increases the intensity (or signal to noise ratio) of the pixels and reduces the horizontal resolution (width) of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningHorizontal | Out | Set number of horizontal photo-sensitive cells to combine together. This increases the intensity (or signal to noise ratio) of the pixels and reduces the horizontal resolution (width) of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningHorizontalMode_RBV | In | Get the mode to use to combine horizontal photo-sensitive cells together when BinningHorizontal is used. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningHorizontalMode | Out | Set the mode to use to combine horizontal photo-sensitive cells together when BinningHorizontal is used. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningVertical_RBV | In | Get number of vertical photo-sensitive cells to combine together. This increases the intensity (or signal to noise ratio) of the pixels and reduces the vertical resolution (height) of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningVertical | Out | Set number of vertical photo-sensitive cells to combine together. This increases the intensity (or signal to noise ratio) of the pixels and reduces the vertical resolution (height) of the image. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningVerticalMode_RBV | In | Get the mode used to combine horizontal photo-sensitive cells together when BinningVertical is used. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | BinningVerticalMode | Out | Set the mode used to combine horizontal photo-sensitive cells together when BinningVertical is used. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReverseX | Out | Flip horizontally the image sent by the device. The Region of interest is applied after the flipping. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ReverseY | Out | Flip vertically the image sent by the device. The Region of interest is applied after the flipping. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TestPatternGeneratorSelector_RBV | In | Get which test pattern generator is controlled by the TestPattern feature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TestPatternGeneratorSelector | Out | Set which test pattern generator is controlled by the TestPattern feature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TestPattern_RBV | In | Get the type of test pattern that is generated by the device as image source. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TestPattern | Out | Set the type of test pattern that is generated by the device as image source. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | DeviceTemperature | In | Get Device Temperature. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Width_RBV | In | Get width. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Width | Out | Set width. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Height_RBV | In | Get height. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | Height | Out | Set height. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | OffsetX_RBV | In | Get offset X. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | OffsetX | Out | Set offset X. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | OffsetY_RBV | In | Get offset Y. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | OffsetY | Out | Set offset Y. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | PixelFormat_RBV | In | Get pixel Format. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | PixelFormat | Out | Set pixel Format. | 55GA00-PCF-0001
Shutter Line Correction
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineCorrectionEnable | Out | Enable the shutterline correction. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineOffsetEven_RBV | In | Get value of Shutterline Offset Even. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineOffsetEven | Out | Set value of Shutterline Offset Even. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureLinesOffsetEven_RBV | In | Get value of Exposure Lines Offset Even. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureLinesOffsetEven | Out | Set value of Exposure Lines Offset Even. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineOffsetOdd_RBV | In | Get value of Shutterline Offset Odd. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ShutterLineOffsetOdd | Out | Set value of Shutterline Offset Odd. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureLinesOffsetOdd_RBV | In | Get value of Exposure Lines Offset Odd. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | ExposureLinesOffsetOdd | Out | Set value of Exposure Lines Offset Odd. | 55GA00-PCF-0001
Transport Layer Control
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | PayloadSize | In | Get the number of bytes transferred for each image or chunk on the stream channel. This includes any end-of-line, end-of-frame statistics or other stamp data. This is the total size of data payload for a data block. | 55GA00-PCF-0001
$(CBS1) | - | $(CBS2) | - | HWCF | : | MFG | - | $(FGIDX) | - | $(CAMIDX) | - | TLParamsLocked | In | Check if the Transport Layer is locked to prevent critical features changes during acquisition. | 55GA00-PCF-0001

## Camera (Baumer VLXT-17M)_S
$(CBS1) | D1
$(CBS2) | N9
$(FGIDX) | 0
$(CAMIDX) | 0

## Voltage Board (Caen A2553)
Variable name | [14 empty] | In/Out In - from device Out - to device | Description | Hardware Allocation
Device
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ErrorSev |  |  |  |  | In | Get error severity
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ErrorSrc |  |  |  |  | In | Get error source
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | ErrorMsg |  |  |  |  | In | Get error message
State Machine
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | StateMachine | - | getState |  |  | In | Get device state (NDS State Machine)
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | StateMachine | - | setState |  |  | Out | Set device state (NDS State Machine)
Board
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | BdStatus |  |  |  |  | In | Status Monitoring
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | OnGroup |  |  |  |  | In | Turn ON channel associated to the selected group
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | OffGroup |  |  |  |  | In | Turn OFF channel associated to the selected group
Channel
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(CHID) |  | ChannelName |  |  | Out | Set Channel Name
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(CHID) |  | V0SET |  |  | Out | Set output voltage Value
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(CHID) |  | VMON |  |  | In | Monitored Voltage Value
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(CHID) |  | Status |  |  | In | Get Status
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(CHID) |  | Power | - | On | Out | Power On the channel
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(CHID) |  | Version | - | Off | Out | Power Off the channel
$(CBS1) | - | $(CBS2) | - | HWCF | : | $(BOARDTYPE) | - | $(BOARDTYPEIDX) | - | $(CHID) |  | Temp |  |  | In | Channel Temperature

## Voltage Board (Caen A2553)_S
$(CBS1) | D1
$(CBS2) | N9
$(BOARDTYPE) | VOLT
$(BOARDTYPEIDX) | 0 | 1
$(CHID) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7