304293-R000XX

Revision A

I&C Environmental Monitoring Specification & Design

Sponsored by XXXX

Under Subcontract No: S0XXX

Prepared by General Atomics

PO Box 85608

San Diego, CA  92186-5608

GA PROJECT 30424

REVISION HISTORY

| Revision | Date | Description of Changes |
| --- | --- | --- |
| A | See Watermark | Initial Release |

POINT OF CONTACT INFORMATION

| PREPARED BY: |  |  |  |
| --- | --- | --- | --- |
| Name | Position | Email | Phone |
| Sebastian Miranda | I&C Engineer |  |  |
| APPROVED BY: |  |  |  |
| Name | Position | Email | Phone |
| Maithili Groh | I&C Engineer | Maithili.Groh@ga.com | 858-455-3532 |

# TABLE OF CONTENTS

REVISION HISTORY	ii

POINT OF CONTACT INFORMATION	ii

ACRONYMS	vii

1	introduction	10

1.1	Purpose	10

1.2	Template Description	10

2	Subsystem overview	10

2.1	I&C Subsystem Overview	10

2.2	System Interfaces	10

2.3	Special Design Considerations	10

2.4	Design Rationalization	10

2.5	Calibration requirements	11

3	System Architecture & Design	11

3.1	System Architecture	11

3.2	Control strategy & Operational Scenarios	11

4	Electrical circuit diagram	12

5	testing	12

6	BOM	12

7	Obsolescence management	12

8	IO Reference Documents	12

9	References	13

# LIST OF FIGURES

Figure 1. 55.GA cable distances to building 74	9

Figure 2. Thermocouple interface with Analog Module and S7-1500 PLC	10

Figure 3. High level view of temperature monitor control scheme	11

# LIST OF Tables

Table 1. 55.GA Transmission line thermocouples	9

Table 2. 55.GA Use cases requirements and functions relating to environmental monitoring	10

Table 3. List of possibles errors and alarms	12

Table 4. Test Plan	13

Table 5. Environmental Monitor BOM	14

Table 6. Environmental Monitoring HMI Variables	14

ACRONYMS

| Acronym | Description |
| --- | --- |
| ADC | Analog to Digital Converter |
| ADC | Analog to Digital Converter |
| AGC | Automatic Gain Control |
| AMC | Advance Mezzanine Module |
| AOM | Acousto-Optical Modulator |
| CBD | Cabling Diagram |
| CDA | Clean Dry Air |
| CO2 | Carbon-dioxide laser |
| CODAC | Control, Data Access and Communication |
| COTS | Commercial Off-The-Shelf |
| cRIO | compact Real-time Input-Output |
| CU | Cubicle (Instrumentation) |
| CWS | Chilled Water Supply |
| D* | Detector Sensitivity |
| DAN | Data Archive Network |
| DC | Direct Current Voltage |
| DDS | Direct Digital Synthesis |
| DIII-D | Tokamak located in San Diego, CA |
| DPD | Digital Phase Demodulator |
| DSP | Digital Signal Processing |
| ENV | TIP Environmental Control Cubicle |
| EPICS | Experimental Physics and Industrial Control System |
| FDR | Final Design Review |
| FMC | FPGA Mezzanine Connector |
| FPGA | Field-Programmable Gate Array |
| FSM | Fast Steering Mirror |
| I&C | Instrumentation & Control |
| IF | Intermediate Frequency |
| IQ | In-Phase, Quadrature-Phase |
| IR | Infra-Red |
| LAN | Local Area Network |
| LCC | Local Controller Cubicle |
| MCB | Miniature Circuit Breakers |
| MHz | Mega-Herz |
| OS | Operating System |
| P&ID | Piping & Instrumentation Diagram |
| PA | Power Amplifier |
| PCDH | Plant Systems Design Handbook |
| PCF | Fast Controller |
| PCF | Fast Plant Controller |
| PCS | Plasma Control System |
| PCSS | Port Cell Support Structure |
| PDR | Preliminary Design Review |
| PFD | Process Flow Diagram |
| PoE | Power Over Ethernet |
| PON | Plant Operations Network |
| PSD | Position Sensing Detector (optical) |
| PSH | Plant System Host |
| PSM | Piezo Steering Mirror |
| QCL | Quantum Cascade Laser |
| QSBA | Quasi-Static Beam Alignment System |
| R&L | Right & Left Circular Polarization |
| RF | Radio Frequency |
| RMS | Root Mean Square |
| SDN | Synchronous Data Network |
| SLD | Single Line Diagram |
| SLO | Synchronous Local Oscillator |
| SPS | Samples per Second |
| SST | Stainless Steel |
| TCN | Timing Control Network |
| TEC | Thermo-Electric Cooler |
| TIP | Toroidal Interferometer Polarimeter |
| TTL | Transistor to Transistor Logic |
| U | Vertical Unit of Rack Space (1.75") |
| VAC | Voltage, Alternating Current |
| VCXO | Voltage Controlled Crystal Oscillator |
| VGA | Variable Gain Amplifier |
| VSWR | Voltage Standing Wave Ratio |

# introduction

## Purpose

This Document outlines the I&C design of the Environmental Monitoring System, with the objective of defining system architecture and components.

# Subsystem overview

## Environmental Control System Overview

Environmental Monitoring subsystem consists of temperature sensors mounted along the UWAVS transmission line and optics, including DSM, Interspace, bio-shield, and Back End Optics and Cameras (BEOC) assembly located in the Port Cell.

Thermocouples are mounted on transmission line structure and on select mirrors and optics. The temperatures captured in mirrors are used as thermal background calibration to be applied to images captured on IR cameras, as a part of calibration process. The thermocouples mounted on the structures such as IOT are used to monitor the local temperature and general trends.

All the sensors are monitored by Siemens PLC located in the Diagnostic Hall “Support Cubicle” [R00030]. The cabling diagrams show the connection to thermocouples in detail. [CBD].

## Special Design Considerations

The temperature sensors placed in vessel, interspace, and port cell are subject to high temperatures and radiation exposure. Therefore, sensors in these areas are required to be radiation hardened.

Thermocouples placed in the in-vessel vacuum environment in A10, A20, and A30 sub assemblies must use mineral insulated cables (MIC) due to high radiation and high temperature environment in these modules. Standard thermocouple wire may be used for the remainder of the system outside of vacuum.

## Design Rationalization

The environmental sensors need to be radiation hardened and this automatically limits the selection pool for these sensors and vendors.

ITER has approved the use of N-type thermocouples in the Port Cell and radiation hardened environment. 55.GA will be using N-type thermocouples specified by ITER.

Normally, considering the long distances between deployment on thermocouples in UWAVS beamline to the acquisition in the diagnostic hall Siemens PLC, transmitters would be needed. But due to failure of electronics in the radiation hardened environment, they can’t be used. ITER has performed prototyping to connect the N type thermocouples directly to Siemens PLC Analog module to show the signal integrity and measurement accuracy are not affected over long distance, up to 200m [8MV2HY].

There are 5 UWAVS ports and each port is at different locations and distance from building 74 where diagnostic hall is located.  All ports are less than 200m from the diagnostic hall where Siemens PLC is located. The locations and distances are shown in Figure 1 .

Figure 1. 55.GA cable distances to building 74

# System Architecture & Design

## System Architecture

The thermocouples are mounted in structure and optics throughout the UWAVS ports. The location of thermocouples in UWAVS ports and quantity is shown in Table 1. For more details refer to [PID].

Table 1. 55.GA Transmission line thermocouples

| Region | UWAVS Component | Thermocouple Quantity |
| --- | --- | --- |
| In Vessel | FMU: Aperture | 1 |
|  | FMU:A10 | 2 |
|  | A20: Shield Module #2 | 2 |
|  | A30: Shield Module #4 | 1 |
|  | A30: Shield Module #5 | 1 |
|  | A30: Shield Module #6 | 1 |
|  | A30: Shield Module #7 | 1 |
| Interspace | IOT Structure | 4 |
|  | A40: Assembly M1 | 3 |
|  | A40: Assembly M2 | 3 |
|  | A50:Assembly M1 | 3 |
|  | A50:Assembly M2 | 3 |
|  | A50:Assembly M3 | 3 |
|  | A50:Assembly M4 | 3 |
| Bio-Shield | A60 | 6 |
| Port Cell | BEOC | 12 |

There are total of 49 thermocouples that are part of the Environmental Monitoring system. The thermocouples are connected to Siemens PLC S7-1500 during installation / commissioning phase. The data is acquired on PLC continuously after installation of the Environmental Monitoring System. The Siemens PLC S7-1500 is shared between many other UWAVS I&C equipment including thermocouples. The architecture is shown in Figure 2.

Figure 2. Thermocouple interface with Analog Module and S7-1500 PLC

## Monitoring strategy & Operational Scenarios

The need for environmental sensors dispersed throughout the beamline can be mapped to the following requirements and use cases in Table 2.

Table 2. 55.GA Use cases requirements and functions relating to environmental monitoring

| Use case | Requirement | Function |
| --- | --- | --- |
| D1-N9-UC-003 | D1-N9-MER-BCT-038 | GAD0-DME-BCO-FW-ST-I1-MEAS, GAD0-DME-BCO-FW-ST-I2-MEAS |
| D1-N9-UC-004 | D1-N9-MER-MPC-014 | GAD0-DME-MPC-TI-EL-ME |
| D1-N9-UC-005 | D1-N9-MER-BCT-032 | GAD0-DME-BCO-II-DI-ME, GAD0-DME-BCO-II-TI-ME |
| D1-N9-UC-006 | D1-N9-MER-BCT-032 | GAD0-DME-BCO-II-DI-ME, GAD0-DME-BCO-II-TI-ME |
| D1-N9-UC-007 | D1-N9-MER-BCT-053 | GAD0-DME-BCO-TI-LH-ME |
| D1-N9-UC-008 | D1-N9-MER-ACT-024 | GAD0-DME-ACO-HL-ST-I1-MEAS, GAD0-DME-ACO-HL-ST-I2-MEAS |
| D1-N9-UC-009 | D1-N9-MER-PSD-007 | GAD0-DME-PHY-FW-ST-I1-MEAS, GAD0-DME-PHY-FW-ST-I2-MEAS |
| D1-N9-UC-010 | D1-N9-MER-MTR-001 | GAD0-DME-OMP-IV-WI-ME |
| D1-N9-UC-014 | D1-N9-MER-PSD-007 | GAD0-DME-PHY-FW-ST-I1-MEAS, GAD0-DME-PHY-FW-ST-I2-MEAS |

Thermocouples are used for passive monitoring of temperature in different parts of UWAVS port and different optics. The typical monitoring strategy involves setting up the data acquisition rate from thermocouples by interfacing with Siemens PLC S7-1500 and acquiring real time, time stamped data. The thermal analysis data [refer to Mike Simon], is used to set the high/low temperature trigger alarms.  There are no interlocks to other UWAVS systems because of alarms but only used for post processing and maintenance purposes.

Figure 3. High level view of temperature monitor control scheme

During the commissioning phase the thermocouples are set up with data acquisition rate and temperature is monitored to establish expected response and eliminate faulty thermocouples or interfacing to the PLC.

The historical data for temperature trends for each thermocouple is monitored during the lifetime of ITER to monitor the drift and wear. The thermocouples may be replaced during large maintenance windows based on feedback from UWAVS physicists. Usefulness and need for a drift detection algorithm may be evaluated in the manufacturing phase. Thermocouple data may also be used in future to evaluate failure of cooling lines in A10,A20,A30 UWAVS modules.

The environmental monitoring data is gathered continuously and streamed on CODAC PON after installation at commissioning phase.

Possible exceptions, alarms and error handling is provided in Table 3.

Table 3. List of possibles errors and alarms

| Error Type | Description | Possible Causes | Alarm |  | Error Handling | Alarm Response |
| --- | --- | --- | --- | --- | --- | --- |
| Open Circuit/ Disconnected | Thermocouple input missing or disconnected | Broken wire, loose terminal, thermocouple unplugged |  | Sensor Fault Alarm | 1. Flag for maintenance 2. Use pre determined value as thermocouple input until replaced. | Show "OPEN" |
| Sensor Shorted | Thermocouple inputs shorted. e.g wire to wire, to grounded surfaces | Pinched wire, installation damage |  | Sensor Fault Alarm | 1. Flag for maintenance 2. Use pre determined value as thermocouple input until replaced. | Show "SHORT" |
| Out of range reading | Reading outside Thermocouple range (Type N: -40°C to 1300°C ) | Faulty thermocouple, signal distortion |  | Input Range Alarm | 1. Flag for maintenance 2. Use pre determined value as thermocouple input until replaced | Show "Invalid Value" |
| High Temperature Warning | Temperature exceeds defined warning threshold | Normal operating temperature approaching upper limits, |  | High Temperature Warning | 1.Flag for maintenance and physicist during post processing of data. | Show Visual/ audible warning on HMI (highlight temperature/ thermocouple ID) |
| Overtemperature Fault | Critical temperature limit exceeded | Cooling failure, runaway process |  | Overtemperature Alarm |  | Raise alarm on HMI for operator action. |
| Communication Failure | Link to PLC,CPU,or CODAC is broken | Cable unplugged, CODAC network down |  | Communication Alarm | 1. Flag for maintenance 2. Use pre determined value as thermocouple input until replaced | "No Data" displayed on HMI |
| Drift or Noise Detected | Fluctuation in readings with constant temperature input | Ground loop, EMI |  | Sensor Stability Warning | 1. Confirm drift or wear using post processing data. 2. Flag for replacement if confirmed. |  |
| Calibration error | Values constantly offset from known standard | Thermocouple degraded/failing |  | Calibration Warning | 1. Confirm drift or wear using post processing data. 2. Flag for replacement if confirmed. | Recommend recalibration/ replacement |

As thermocouples are configured at commissioning and gather data continuously, they operate in all plant state operating states (PSOS) specified in the [SDS].

# testing

Commissioning test plan for thermocouples is shown in Table 4.

Table 4. Test Plan

| Test ID | Commissioning 1 |
| --- | --- |
| WAVS Area | Diagnostic First Wall(DFW), Diagnostic Shield Module(DSM), Interspace, Bio-shield, Port Cell |
| Component | Thermocouples |
| Purpose | Check Functionality of temperature monitoring system |
| Verification | Document review, test to validate component |
| Description | •Validate electrical performance, signal accuracy, and functionality of hardware. •Verify measurement stability in room conditions •Verify Data transmission/storage |
| Support Equipment | Controller units and Cables |
| Test Conditions | Room Conditions |

# ENVIRONMENTAL Monitoring SYstem BOM

Table 5. Environmental Monitor BOM

| Device | Manufacturer Number/ ITER Part Number | Quantity |
| --- | --- | --- |
| Thermocouple Type N | Thermocoax | 49 |
| 8 Analog Input Module U/I/RTD/TC | SM531-8AI / 6ES7531-7PF00-0AB0 | 7 |
| PM 1507 24V/3A power module | 6EP1332-4BA00 | 1 |
| S7-1500 | 6ES7516-3AN01-0AB0 | 1 |

# Obsolescence management

Please refer to ITER_D_PQM7M8 for Obsolescence management on Slow Controller I/O. As UWAVS is using N type thermocouples referred by ITER, UWAVS will reply on obsolescence plan developed by ITER for N type thermocouples.

# HMI variables

Table 6. Environmental Monitoring HMI Variables

| Variable Type | Variable Name | Description | Typical Format example |
| --- | --- | --- | --- |
| Real Time Monitoring | Temp_CH_# | Real time reading from thermocouple in assigned channel | 70.0°C |
|  | Status_CH_# | Sensor State | OK, OPEN, SHORT |
| Alarm and Warning | HI_Temp_CH_# | High temperature Alert, Approaching Upper Limit | TRUE/FALSE |
|  | LO_Temp_CH_# | Low temperature Alert, Approaching Lower Limit | TRUE/FALSE |
|  | CRIT_HI_Temp_CH_# | Critical Temperature Alert, Above Upper Limit | TRUE/FALSE |
|  | CRIT_LO_Temp_CH_# | Critical Temperature Alert, Below Lower Limit | TRUE/FALSE |
|  | Comm_Loss | Loss of Communication with controller/CODAC | TRUE/FALSE |
| Control and Configuratrion | TEMP_OFFSET_CH_# | Manual adjustment of temperature offset | -1.4°C |
|  | Logging Interval | Manual adjustment between log entries | 5 seconds |

# References

| [2] | 55-GA-A0 IR Cameras: VIS/IR TV (Upper) UPP02 PID, ITER_D_PJ4JFG, v2.0. |
| --- | --- |
| [3] | 55-GA-B0 IR Cameras: VIS/IR TV (Upper) UPP08 PID, ITER_D_PJAC7P, v1.0. |
| [4] | 55-GA-D0 IR Cameras: VIS/IR TV (Upper) UPP14 PID, ITER_D_PHUE63, v1.0. |
| [5] | 55-GA-EO IR Cameras: Vis/IR TV (Upper) UPP14 PID, ITER_D_PJB95T, v1.0. |
| [6] | 55-GA-A0 IR Cameras: VIS/IR (Upper) UPP02 Cabling, ITER_D_3QQP6T, v2.2. |
| [7] | 55-GA-B0 IR Cameras: VIS/IR (Upper) UPP08 Cabling, ITER_D_3QSJ6B, v2.4. |
| [8] | 55-GA-C0 IR Cameras: VIS/IR (Upper) UPP11 Cabling, ITER_D_596WA5, v2.0. |
| [9] | 55-GA-D0 IR Cameras: VIS/IR (Upper) UPP14 Cabling, ITER_D_3QSD6R, v2.0. |
| [23] | 55.GA UWAVS I&C System Design Specification, 304243-S00025, Rev A, ITER_D_ARS734, v1.0. |
| [25] | UWAVS Calibration Plan, 304243-V00057, Rev A, ITER_D_C8HP3D, V1.0. |
| [30] | I&C Cubicle Internal Configuration, ITER_D_4H5DW6, v4.1. |
| [31] | 55.EC-I&C Cubicle Configuration, YSMSJH, V2.1. |
| [40] | 55.GA UWAVS I&C System Requirement Specification, 304243-S00024, Rev A, ITER_D_ARRY56, v1.0. |

Please list references.

55.GA - Surface Temperature Measurement and Data Analysis Research and Development Report (UWAV2), ITER_D_YWS8ZC

FBS specification for thermocouple monitoring system, ITER_D_ADAVQH, v1.1

N Type Thermocouple, ITER_D_64J7S9, v1.0

I&C Cubicle Internal Configuration, ITER_D_PQM7M8, v1.0

55.GA_UWAVS-35_System_Detailed_Performance_Definition_rel, 304243-R00018, Rev B