## Components
Component ID | Component Name* | Description | Comment | Quality | Location | PA | In Cubicle | Controller | Mnemonic Name |  |  | TO BE ADDED
D1-N9-GAD0-COMP-001 | 55GAD0-CU-7302 | Local Control Cubicle for UP#14 |  | confirmed good | 74-L2-04 | PA 5.5.P3.US.01 | N/A | N/A |  |  | Tag | Description | Location
D1-N9-GAD0-COMP-002 | 55GAD0-PLC-9003 | Cubicle monitoring with Siemens Simatic PLC | Siemens Simatic S7-1200 | confirmed good | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7301 | N/A |  |  | MZH-0323 | high limit switch | valve box | DONE
D1-N9-GAD0-COMP-003 | 55GAD0-SWT-9003 | Managed 24-port Full Gigabit 19" Switch with redundant PSU | Hirschmann MACH 104, mach104-20tx-fr HIR942003101 | confirmed good | 74-L1-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7301 | N/A |  |  | MZL-0323 | low limit switch | valve box | DONE
D1-N9-GAD0-COMP-004 | 55GAD0-PCF-9003 | I&C Grade HDEC PC 4U Computer | ID01549-A-006/ITER (Master Controller) | confirmed good | 74-L1-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | N/A |  | Already in diagram | ATG-0010 | general actuator valve | valve box | DONE
D1-N9-GAD0-COMP-005 | 55GAD0-PCF-9004 | DAQ Grade HDEC PC 4U Computer | ID01812-B-001/ITER #1 | confirmed good | 74-L1-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7301 | N/A |  |  | MP-0001 | pressure transmitter | valve box | DONE
D1-N9-GAD0-COMP-006 | 55GAD0-PCF-9002 | DAQ Grade HDEC PC 4U Computer | ID01812-B-001/ITER #2 | confirmed good | 74-L1-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7301 | N/A |  |  | MZH-0315 | high limit switch | valve box | DONE
D1-N9-GAD0-COMP-007 | 55GAD0-DAS-9002 | MTCA.4 Chassis #1 | MTCA-12-2P-ML | confirmed good | 74-L1-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7301 | 55GAD0-PCF-9003 |  |  | MZL-0315 | low limit switch | valve box | DONE
D1-N9-GAD0-COMP-008 | 55GAD0-DAS-9003 | MTCA.4 Chassis #2 | MTCA-12-2P-ML | confirmed good | 74-L1-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7301 | 55GAD0-PCF-9004 |  |  | ATG-0315 | general actuator valve | valve box | DONE
D1-N9-GAD0-COMP-009 | 55GAD0-CCD-3201 | Infrared Camera #1 | TBD | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PCF-9003 |  | Not in diagram/Need to be removed from sheet | MZH-0317 | high limit switch | valve box | DONE
D1-N9-GAD0-COMP-010 | 55GAD0-CCD-3203 | Infrared Camera #2 | TBD | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PCF-9003 |  |  | MZL-0317 | low limit switch | valve box | DONE
D1-N9-GAD0-COMP-011 | 55GAD0-CCD-3202 | Visible Camera #1 | TBD | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PCF-9004 |  |  | ATG-0317 | general actuator valve | valve box | DONE
D1-N9-GAD0-COMP-012 | 55GAD0-CCD-3204 | Visible Camera #2 | TBD | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PCF-9004 |  |  | MP-0004 | pressure transmitter | valve box | DONE
D1-N9-GAD0-COMP-013 | 55GAD0-PSU-9006 | Power Supply | Caen SY5527LC | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 74-L2-08 | 55GAD0-PCF-9002 |  | Tag need checking | MZH-0319 | high limit switch | valve box | DONE
D1-N9-GAD0-COMP-014 | 55GAD0-MTE-1101 | Thermocouple: N Type | A10 Thermocouple | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | MZL-0319 | low limit switch | valve box | DONE
D1-N9-GAD0-COMP-015 | 55GAD0-MTE-1102 | Thermocouple: N Type | A10 Thermocouple | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | ATG-0319 | general actuator valve | valve box | DONE
D1-N9-GAD0-COMP-016 | 55GAD0-MTE-1103 | Thermocouple: N Type | A10 Thermocouple | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | MP-0002 | pressure transmitter | valve box | DONE
D1-N9-GAD0-COMP-017 | 55GAD0-CSO-1101 | Calibration source: filament | A10 Calibration source | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  | Newly added/Edited | MZH-0321 | high limit switch | valve box | DONE
D1-N9-GAD0-COMP-018 | 55GAD0-CSO-1102 | Calibration source: filament | A10 Calibration source | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | MZL-0321 | low limit switch | valve box | DONE
D1-N9-GAD0-COMP-019 | 55GAD0-MTE-1201 | Thermocouple: N Type | A20 Thermocouple | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | ATG-0321 | general actuator valve | valve box | DONE
D1-N9-GAD0-COMP-020 | 55GAD0-MTE-1202 | Thermocouple: N Type | A20 Thermocouple | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | MZH-0301 | high limit switch | valve box | DONE
D1-N9-GAD0-COMP-021 | 55GAD0-MTE-1401 | Thermocouple: N Type | A30 Thermocouple | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  | Needs priority attention | MZL-0301 | low limit switch | valve box | DONE
D1-N9-GAD0-COMP-022 | 55GAD0-MTE-1501 | Thermocouple: N Type | A30 Thermocouple | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | ATG-0301 | general actuator valve | valve box | DONE
D1-N9-GAD0-COMP-023 | 55GAD0-MTE-1601 | Thermocouple: N Type | A30 Thermocouple | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | MZH-0322 | high limit switch | valve box | DONE
D1-N9-GAD0-COMP-024 | 55GAD0-MTE-1701 | Thermocouple: N Type | A30 Thermocouple | unconfirmed | CST-S07-UPR_14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | MZL-0322 | low limit switch | valve box | DONE
D1-N9-GAD0-COMP-025 | 55GAD0-MTE-2001 | Thermocouple: N Type | Window Thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | ATG-0322 | general actuator valve | valve box | DONE
D1-N9-GAD0-COMP-026 | 55GAD0-MTE-2002 | Thermocouple: N Type | Window Thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-027 | 55GAD0-MTE-2003 | Thermocouple: N Type | Window Thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | - | IR Cam-1 media converter | Shielded Electronics Rack | DONE
D1-N9-GAD0-COMP-028 | 55GAD0-MTE-2004 | Thermocouple: N Type | Window Thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | - | IR Cam-2 media converter | Shielded Electronics Rack | DONE
D1-N9-GAD0-COMP-029 | 55GAD0-MTE-2101 | Thermocouple: N Type | IOT structure thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | - | VIS Cam-1 media converter | Shielded Electronics Rack | DONE
D1-N9-GAD0-COMP-030 | 55GAD0-MTE-2102 | Thermocouple: N Type | IOT structure thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | - | VIS Cam-2 media converter | Shielded Electronics Rack | DONE
D1-N9-GAD0-COMP-031 | 55GAD0-MTE-2103 | Thermocouple: N Type | IOT structure thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | - | AM-1 media converter | Shielded Electronics Rack | DONE
D1-N9-GAD0-COMP-032 | 55GAD0-MTE-2104 | Thermocouple: N Type | IOT structure thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002 |  |  | - | AM-2 media converter | Shielded Electronics Rack | DONE
D1-N9-GAD0-COMP-033 | 55GAD0-MTE-2105 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-034 | 55GAD0-MTE-2106 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-035 | 55GAD0-MTE-2107 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-036 | 55GAD0-MTE-2108 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-037 | 55GAD0-MTE-2109 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-038 | 55GAD0-MTE-2110 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-039 | 55GAD0-MTE-2111 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-040 | 55GAD0-MTE-2112 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-041 | 55GAD0-MTE-2113 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-042 | 55GAD0-MTE-2114 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-043 | 55GAD0-MTE-2115 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-044 | 55GAD0-MTE-2116 | Thermocouple: N Type | A50 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-045 | 55GAD0-MTE-2301 | Thermocouple: N Type | A40 M1 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-046 | 55GAD0-MTE-2302 | Thermocouple: N Type | A40 M1 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-047 | 55GAD0-MZL-2301 | Low limit switch | A40 M1 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-048 | 55GAD0-MZH-2301 | high limit switch | A40 M1 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-049 | 55GAD0-MZL-2302 | Low limit switch | A40 M1 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-050 | 55GAD0-MZH-2302 | high limit switch | A40 M1 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-051 | 55GAD0-GM-2301 | Motor | A40 M1 motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-052 | 55GAD0-GM-2302 | Motor | A40 M1 motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-053 | 55GAD0-MTE-2401 | Thermocouple: N Type | A40 M2 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-054 | 55GAD0-MTE-2402 | Thermocouple: N Type | A40 M2 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-055 | 55GAD0-MTE-2403 | Thermocouple: N Type | A40 M2 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-056 | 55GAD0-MZL-2401 | Low limit switch | A40 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-057 | 55GAD0-MZH-2401 | high limit switch | A40 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-058 | 55GAD0-MZL-2402 | Low limit switch | A40 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-059 | 55GAD0-MZH-2402 | high limit switch | A40 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-060 | 55GAD0-MZL-2403 | Low limit switch | A40 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-061 | 55GAD0-MZH-2403 | high limit switch | A40 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-062 | 55GAD0-GM-2401 | Motor | A40 M2 motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-063 | 55GAD0-GM-2402 | Motor | A40 M2 motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-064 | 55GAD0-GM-2403 | Motor | A40 M2 motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9003
D1-N9-GAD0-COMP-065 | 55GAD0-MTE-2201 | Thermocouple: N Type | BOL structure thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-066 | 55GAD0-MTE-2202 | Thermocouple: N Type | BOL structure thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-067 | 55GAD0-MTE-2501 | Thermocouple: N Type | A60 M2 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-068 | 55GAD0-MTE-2502 | Thermocouple: N Type | A60 M2 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-069 | 55GAD0-MZH-2501 | high limit switch | A60 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-070 | 55GAD0-MZL-2501 | Low limit switch | A60 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-071 | 55GAD0-MZH-2502 | high limit switch | A60 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-072 | 55GAD0-MZL-2502 | Low limit switch | A60 M2 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-073 | 55GAD0-GM-2501 | Motor | A60 M2 motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-074 | 55GAD0-GM-2502 | Motor | A60 M2 motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-075 | 55GAD0-MTE-2503 | Thermocouple: N Type | A60 M1 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-076 | 55GAD0-MTE-2504 | Thermocouple: N Type | A60 M1 Assembly thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-077 | 55GAD0-MZH-2503 | high limit switch | A60 M1 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-078 | 55GAD0-MZL-2503 | Low limit switch | A60 M1 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-079 | 55GAD0-MZH-2504 | high limit switch | A60 M1 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-080 | 55GAD0-MZL-2504 | Low limit switch | A60 M1 Assembly limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-081 | 55GAD0-GM-2503 | Motor | A60 M1 motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-082 | 55GAD0-GM-2504 | Motor | A60 M21 motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-083 | 55GAD0-MZS-3301 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-084 | 55GAD0-MZS-3302 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-085 | 55GAD0-MZS-3303 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-086 | 55GAD0-MZS-3304 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-087 | 55GAD0-MZS-3305 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-088 | 55GAD0-MZS-3306 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-089 | 55GAD0-MZH-3202 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-090 | 55GAD0-MZL-3202 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-091 | 55GAD0-MZH-3204 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-092 | 55GAD0-MZL-3204 | limit switch | Filter Wheel home switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-093 | 55GAD0-GM-3301 | Motor | Filter wheel motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-094 | 55GAD0-GM-3302 | Motor | Filter wheel motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-095 | 55GAD0-GM-3303 | Motor | Filter wheel motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-096 | 55GAD0-GM-3304 | Motor | Filter wheel motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-097 | 55GAD0-GM-3305 | Motor | Filter wheel motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-098 | 55GAD0-GM-3306 | Motor | Filter wheel motor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-099 | 55GAD0-MTE-3101 | Thermocouple: N Type | Calibration Assembly thermocouple: BB source | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-100 | 55GAD0-MTE-3102 | Thermocouple: N Type | Calibration Assembly thermocouple : BB source | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-101 | 55GAD0-MTE-3103 | Thermocouple: N Type | Calibration Assembly thermocouple : IS source | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-102 | 55GAD0-MTE-3104 | Thermocouple: N Type | Calibration Assembly thermocouple : IS source | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-103 | 55GAD0-MTE-3105 | Thermocouple: N Type | Diachromatic splitter thermocouple | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-104 | 55GAD0-CSO-3101 | Calibration source : Blackbody | Calibration source | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-SCI-9101
D1-N9-GAD0-COMP-105 | 55GAD0-CSO-3102 | Calibration source: Integrated sphere | Calibration source | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-SCI-9101
D1-N9-GAD0-COMP-106 | 55GAD0-MTE-3201 | Thermocouple: N Type | A70 W1 Temperature | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-107 | 55GAD0-MTE-3202 | Thermocouple: N Type | A70 S1 Temperature | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-108 | 55GAD0-MTE-3203 | Thermocouple: N Type | A80 temperature : Spare | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-109 | 55GAD0-MTE-3204 | Thermocouple: N Type | CAM optics bench temperature | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-110 | 55GAD0-MTE-3205 | Thermocouple: N Type | CAM optics bench temperature | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-111 | 55GAD0-MTE-3206 | Thermocouple: N Type | CAM optics bench temperature | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-112 | 55GAD0-MTE-3207 | Thermocouple: N Type | CAM optics bench temperature | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-113 | 55GAD0-MTE-3208 | Thermocouple: N Type | Temperature : spare | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-114 | 55GAD0-MTE-3209 | Thermocouple: N Type | Temperature : spare | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-115 | 55GAD0-MTE-3210 | Thermocouple: N Type | Temperature : spare | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-116 | 55GAD0-GM-3202 | Motor | visible camera linear stage | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-117 | 55GAD0-GM-3204 | Motor | visible camera linear stage | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-CMO-9001
D1-N9-GAD0-COMP-118 | 55GAD0-MZH-3202 | high limit switch | visible camera linear stage high limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-119 | 55GAD0-MZL-3202 | Low limit switch | visible camera linear stage low limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-120 | 55GAD0-MZH-3204 | high limit switch | visible camera linear stage high limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-121 | 55GAD0-MZL-3204 | Low limit switch | visible camera linear stage low limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-122 | 55GAD0-RCK-3100 | RF macthing box | RF matching box 1 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | Shielded Electronics Rack | 55GAD0-PSU-9212
D1-N9-GAD0-COMP-123 | 55GAD0-RCK-3200 | RF macthing box | RF matching box 2 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | Shielded Electronics Rack | 55GAD0-PSU-9214
- | TBD | RF active matching media converter | RF matching box 1 media converter | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.02 | Shielded Electronics Rack | N/A
- | TBD | RF active matching media converter | RF matching box 2 media converter | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.03 | Shielded Electronics Rack | N/A
- | TBD | Camera Media Converter | IR CAM1 Media converter | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.04 | Shielded Electronics Rack | N/A
- | TBD | Camera Media Converter | IR CAM2 Media converter | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.05 | Shielded Electronics Rack | N/A
- | TBD | Camera Media Converter | VIS CAM1 Media Converter | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.06 | Shielded Electronics Rack | N/A
- | TBD | Camera Media Converter | VIS CAM2 Media Converter | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.07 | Shielded Electronics Rack | N/A
D1-N9-GAD0-COMP-124 | 55GAD0-MPE-7073 | Pressure sensor | Chilled water pressure sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-125 | 55GAD0-MTE-7373 | Thermocouple: N Type | Chilled water temperature sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-126 | 55GAD0-MPE-7075 | Pressure sensor | Chilled water pressure sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-127 | 55GAD0-MPE-7076 | Thermocouple: N Type | Chilled water temperature sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-128 | 55GAD0-MFE-7074 | flow sensor | Chilled water flow sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-129 | 55GAD0-ATC-1008 | Actuator | Chilled water valve actuator | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-130 | 55GAD0-MPE-7071 | Pressure sensor | Chilled water pressure sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-131 | 55GAD0-MTE-7371 | Thermocouple: N Type | Chilled water temperature sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-132 | 55GAD0-MPE-7072 | Pressure sensor | Chilled water pressure sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-133 | 55GAD0-MPE-7071 | Thermocouple: N Type | Chilled water temperature sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-134 | 55GAD0-MFE-7073 | flow sensor | Chilled water flow sensor | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-135 | 55GAD0-ATC-1007 | Actuator | Chilled water valve actuator | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-136 | 55GAD0-PSU-9211 | RF generator 1 | RF generator | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
D1-N9-GAD0-COMP-137 | 55GAD0-PSU-9214 | RF generator 2 | RF generator | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
| TBD | Motor | Stepper motor controlled by PLC that will control load cap position | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | Shielded Electronics Rack | 55GAD0-PLC-9002
| TBD | Motor | Stepper motor controlled by PLC that will control tune cap position | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | Shielded Electronics Rack | 55GAD0-PLC-9002
| TBD | limit switch | High limit switch for load cap stepper motor | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | Shielded Electronics Rack | 55GAD0-PLC-9002
| TBD | limit switch | Low limit switch for load cap stepper motor | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | Shielded Electronics Rack | 55GAD0-PLC-9002
| TBD | limit switch | High limit switch for tune cap stepper motor | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | Shielded Electronics Rack | 55GAD0-PLC-9002
| TBD | limit switch | Low limit switch for tune cap stepper motor | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | Shielded Electronics Rack | 55GAD0-PLC-9002
| TBD | VSWR Meter | VSWR meter for measuring reflected power | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | Shielded Electronics Rack | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-138 | 55GAD0-SWT-9001 | Managed 24-port Full Gigabit 19" Switch with redundant PSU | Hirschmann MACH 104, mach104-20tx-fr HIR942003101 | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | N/A
D1-N9-GAD0-COMP-139 | 55GAD0-SWT-9002 | LAN hub | LAN Hub (ITER catalogue) | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | N/A
D1-N9-GAD0-COMP-140 | 55GAD0-PLC-9001 | Cubicle monitoring with Siemens Simatic PLC | Siemens Simatic S7-1200 | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | N/A
D1-N9-GAD0-COMP-141 | 55GAD0-PCF-9001 | I&C grade master controller computer | I&C grade computer | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | N/A
D1-N9-GAD0-COMP-142 | 55GAD0-PSU-9005 | Programmable DC filament PSU | Custom under design | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
D1-N9-GAD0-COMP-143 | 55GAD0-SCI-9101 | filament signal conditioning unit | Custom under design | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
D1-N9-GAD0-COMP-144 | 55GAD0-MTC-9001 | Blackbody oven controller | Mikron M330 blackbodies | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
D1-N9-GAD0-COMP-145 | 55GAD0-CMO-9001 | 12 Axis motor controller | PI C-663. 12C885 | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
D1-N9-GAD0-COMP-146 | 55GAD0-CU-7301 | Local Control Cubicle for UP#14 | Cubicle | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | N/A
D1-N9-GAD0-COMP-147 | 55GAD0-PSU-9001 | DCPS #1 | Keysight N700 | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
D1-N9-GAD0-COMP-148 | 55GAD0-PSU-9002 | DCPS #2 | Keysight N701 | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
D1-N9-GAD0-COMP-149 | 55GAD0-PSU-9003 | DCPS #3 | Keysight N702 | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
D1-N9-GAD0-COMP-150 | 55GAD0-PSU-9004 | DCPS #4 | Keysight N703 | unconfirmed | 74-L2-04 | PA 5.5.P3.US.01 | 55GAD0-CU-7302 | 55GAD0-PCF-9001
- | 55GAD0-MZL-0301 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZH-0301 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZL-0315 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZH-0315 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZL-0317 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZH-0317 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZL-0319 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZH-0319 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZL-0321 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZH-0321 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZL-0322 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZH-0322 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZL-0323 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MZH-0323 | limit switch | pneumatic acturator limit switch | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MP-0001 | Pressure sensor | Pressure measurement at pneumatic control valve | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MP-0002 | Pressure sensor | Pressure measurement at pneumatic control valve | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-MP-0004 | Pressure sensor | Pressure measurement at pneumatic control valve | unconfirmed | 11-L2-C15 | PA 5.5.P3.US.02 | N/A | 55GAD0-PLC-9003
D1-N9-GAD0-COMP-163 | 55GAD0-PL-4401 | Pump | Shutter actuator pump 1 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-164 | 55GAD0-PL-4402 | Pump | Shutter actuator pump 2 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-ATG-0301 | Actuator | Electromagnetic acutator for VG-0301 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-ATG-0315 | Actuator | Electromagnetic acutator for VG-0315 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-ATG-0317 | Actuator | Electromagnetic acutator for VG-0317 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-ATG-0319 | Actuator | Electromagnetic acutator for VG-0319 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-ATG-0321 | Actuator | Electromagnetic acutator for VG-0321 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-ATG-0322 | Actuator | Electromagnetic acutator for VG-0322 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
- | 55GAD0-ATG-0323 | Actuator | Electromagnetic acutator for VG-0323 | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002
D1-N9-GAD0-COMP-171 | 55GAD0-ATC-1010 | Actuator | Chilled water valve actuator | unconfirmed | 11-L2-C14 | PA 5.5.P3.US.01 | N/A | 55GAD0-PLC-9002

## Signals
Signal ID | Signal Name | Component* | Description | Type | Direction | Logic | Range | I&C Cubicle | Quality | Component Destination* | Mnemonic Name
D1-N9-GAD0-SIG-001 | 55GAD0-CCD-3201:CR-CRC | 55GAD0-CCD-3201 | Trigger signal for the IR Camera #1 | A | O | P | 0 +5 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-002 | 55GAD0-CCD-3203:CR-CRC | 55GAD0-CCD-3203 | Trigger signal for the IR Camera #2 | A | O | P | 0 +5 V | 55GAD0-CU-7302 | unconfirmed |  |  | Already in diagram
D1-N9-GAD0-SIG-003 | 55GAD0-CCD-3202:CR-CRC | 55GAD0-CCD-3202 | Trigger signal for the Visible Camera #1 | A | O | P | 0 +5 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-004 | 55GAD0-CCD-3204:CR-CRC | 55GAD0-CCD-3204 | Trigger signal for the Visible Camera #2 | A | O | P | 0 +5 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-005 | 55GAD0-CCD-3201:JT-CRC | 55GAD0-CCD-3201 | Power signal for the IR Camera #1 | A | O | P | 24 V DC | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-006 | 55GAD0-CCD-3203:JT-CRC | 55GAD0-CCD-3203 | Power signal for the IR Camera #2 | A | O | P | 24 V DC | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-007 | 55GAD0-CCD-3202:JT-CRC | 55GAD0-CCD-3202 | Power signal for the Visible Camera #1 | A | O | P | 24 V DC | 55GAD0-CU-7302 | unconfirmed |  |  | Not in diagram/Need to be removed from sheet
D1-N9-GAD0-SIG-008 | 55GAD0-CCD-3204:JT-CRC | 55GAD0-CCD-3204 | Power signal for the Visible Camera #2 | A | O | P | 24 V DC | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-009 | 55GAD0-PSU-8501:ET05-CCC | 55GAD0-PSU-8501 | Trigger signal for the IR Camera #1 (if triggering is not achieved by GigE) | A | O | P | 0 +5 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-010 | 55GAD0-PSU-8501:ET06-CCC | 55GAD0-PSU-8501 | Trigger signal for the IR Camera #2 (if triggering is not achieved by GigE) | A | O | P | 0 +5 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-011 | 55GAD0-PSU-8501:ET07-CCC | 55GAD0-PSU-8501 | Trigger signal for the Visible Camera #1 (if triggering is not achieved by GigE) | A | O | P | 0 +5 V | 55GAD0-CU-7302 | unconfirmed |  |  | Tag need checking
D1-N9-GAD0-SIG-012 | 55GAD0-PSU-8501:ET08-CCC | 55GAD0-PSU-8501 | Trigger signal for the Visible Camera #2 (if triggering is not achieved by GigE) | A | O | P | 0 +5 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-013 | 55GAD0-PSU-8501:ET09-CCC | 55GAD0-PSU-8501 | Power signal for the IR Camera #1 transceiver (if camera is not fiber embedded) | A | O | P | 12 V DC | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-014 | 55GAD0-PSU-8501:ET10-CCC | 55GAD0-PSU-8501 | Power signal for the IR Camera #2 transceiver (if camera is not fiber embedded) | A | O | P | 12 V DC | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-015 | 55GAD0-PSU-8501:ET11-CCC | 55GAD0-PSU-8501 | Power signal for the Visible Camera #1 transceiver (if camera is not fiber embedded) | A | O | P | 12 V DC | 55GAD0-CU-7302 | unconfirmed |  |  | Newly added/Edited
D1-N9-GAD0-SIG-016 | 55GAD0-PSU-8501:ET12-CCC | 55GAD0-PSU-8501 | Power signal for the Visible Camera #2 transceiver (if camera is not fiber embedded) | A | O | P | 12 V DC | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-017 | 55GAD0-MTE-1101:TE-CRC | 55GAD0-MTE-1101 | A10 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-018 | 55GAD0-MTE-1102:TE-CRC | 55GAD0-MTE-1102 | A10 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-019 | 55GAD0-MTE-1103:TE-CRC | 55GAD0-MTE-1103 | A10 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-020 | 55GAD0-WMM-1211:JT-CRC | 55GAD0-WMM-1211 | A10 Aseembly mirror 1 RF input | A | I | P | custom | 55GAD0-CU-7301 | unconfirmed |  |  | Bertan stuff. Don’t touch
D1-N9-GAD0-SIG-021 | 55GAD0-WMM-1211:JT-CRC | 55GAD0-WMM-1211 | A10 Aseembly mirror 1 RF return | A | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-022 | 55GAD0-WMM-1214:JT-CRC | 55GAD0-WMM-1214 | A10 Aseembly mirror 2 RF input | A | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-023 | 55GAD0-WMM-1214:JT-CRC | 55GAD0-WMM-1214 | A10 Aseembly mirror 2 return | A | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-024 | 55GAD0-CSO-1101:ET-CRC | 55GAD0-CSO-1101 | A10 assembly clalibration source voltage | A | I | P | custom | 55GAD0-CU-7301 | unconfirmed |  |  | Need to be revisited/looked at/questions
D1-N9-GAD0-SIG-025 | 55GAD0-CSO-1102:ET-CRC | 55GAD0-CSO-1102 | A10 assembly clalibration source voltage measurement | A | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-026 | 55GAD0-MTE-1201:TE-CRC | 55GAD0-MTE-1201 | A20 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-027 | 55GAD0-MTE-1202:TE-CRC | 55GAD0-MTE-1202 | A20 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-028 | 55GAD0-MTE-1401:TE-CRC | 55GAD0-MTE-1401 | A30 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed |  |  | Needs priority attention
D1-N9-GAD0-SIG-029 | 55GAD0-MTE-1501:TE-CRC | 55GAD0-MTE-1501 | A30 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-030 | 55GAD0-MTE-1601:TE-CRC | 55GAD0-MTE-1601 | A30 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-031 | 55GAD0-MTE-1701:TE-CRC | 55GAD0-MTE-1701 | A30 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-032 | 55GAD0-MTE-1401:TE-CRC | 55GAD0-MTE-1401 | A30 mirror thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-033 | 55GAD0-MTE-2001:TE-CRC | 55GAD0-MTE-2001 | IOT structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-034 | 55GAD0-MTE-2002:TE-CRC | 55GAD0-MTE-2002 | IOT structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-035 | 55GAD0-MTE-2003:TE-CRC | 55GAD0-MTE-2003 | IOT structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-036 | 55GAD0-MTE-2004:TE-CRC | 55GAD0-MTE-2004 | IOT structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-037 | 55GAD0-MZL-2401:ZL-CRC | 55GAD0-MZL-2401 | A40 M2 limit switch | D | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-038 | 55GAD0-MZH-2401:ZH-CRC | 55GAD0-MZH-2401 | A40 M2 limit switch | D | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-039 | 55GAD0-MTE-2401:TE-CRC | 55GAD0-MTE-2401 | A40 M2 thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-040 | 55GAD0-GM-2401:CR-CCC | 55GAD0-GM-2401 | A40 M2 motor A+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-041 | 55GAD0-GM-2401:CR-CCC | 55GAD0-GM-2401 | A40 M2 motor A- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-042 | 55GAD0-GM-2401:CR-CCC | 55GAD0-GM-2401 | A40 M2 motor B+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-043 | 55GAD0-GM-2401:CR-CCC | 55GAD0-GM-2401 | A40 M2 motor B- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-044 | 55GAD0-MZL-2402:ZL-CRC | 55GAD0-MZL-2402 | A40 M2 limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-045 | 55GAD0-MZH-2402:ZH-CRC | 55GAD0-MZH-2402 | A40 M2 limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-046 | 55GAD0-MTE-2402:TE-CRC | 55GAD0-MTE-2402 | A40 M2 thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-047 | 55GAD0-GM-2402:CR-CCC | 55GAD0-GM-2402 | A40 M2 motor A+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-048 | 55GAD0-GM-2402:CR-CCC | 55GAD0-GM-2402 | A40 M2 motor A- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-049 | 55GAD0-GM-2402:CR-CCC | 55GAD0-GM-2402 | A40 M2 motor B+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-050 | 55GAD0-GM-2402:CR-CCC | 55GAD0-GM-2402 | A40 M2 motor B- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-051 | 55GAD0-MZL-2403:ZL-CRC | 55GAD0-MZL-2403 | A40 M2 limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-052 | 55GAD0-MZH-2403:ZH-CRC | 55GAD0-MZH-2403 | A40 M2 limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-053 | 55GAD0-MTE-2403:TE-CRC | 55GAD0-MTE-2403 | A40 M2 thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-054 | 55GAD0-GM-2403:CR-CCC | 55GAD0-GM-2403 | A40 M2 motor A+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-055 | 55GAD0-GM-2403:CR-CCC | 55GAD0-GM-2403 | A40 M2 motor A- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-056 | 55GAD0-GM-2403:CR-CCC | 55GAD0-GM-2403 | A40 M2 motor B+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-057 | 55GAD0-GM-2403:CR-CCC | 55GAD0-GM-2403 | A40 M2 motor B- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-058 | 55GAD0-MZL-2301:ZL-CRC | 55GAD0-MZL-2301 | A40 M1 limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-059 | 55GAD0-MZH-2301:ZH-CRC | 55GAD0-MZH-2301 | A40 M1 limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-060 | 55GAD0-MTE-2301:TE-CRC | 55GAD0-MTE-2301 | A40 M1 thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-061 | 55GAD0-GM-2301:CR-CCC | 55GAD0-GM-2301 | A40 M1 motor A+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-062 | 55GAD0-GM-2301:CR-CCC | 55GAD0-GM-2301 | A40 M1 motor A- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-063 | 55GAD0-GM-2301:CR-CCC | 55GAD0-GM-2301 | A40 M1 motor B+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-064 | 55GAD0-GM-2301:CR-CCC | 55GAD0-GM-2301 | A40 M1 motor B- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-065 | 55GAD0-MZL-2302:ZL-CRC | 55GAD0-MZL-2302 | A40 M1 limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-066 | 55GAD0-MZH-2302:ZH-CRC | 55GAD0-MZH-2302 | A40 M1 limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-067 | 55GAD0-MTE-2302:TE-CRC | 55GAD0-MTE-2302 | A40 M1 thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-068 | 55GAD0-GM-2302:CR-CCC | 55GAD0-GM-2302 | A40 M1 motor A+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-069 | 55GAD0-GM-2302:CR-CCC | 55GAD0-GM-2302 | A40 M1 motor A- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-070 | 55GAD0-GM-2302:CR-CCC | 55GAD0-GM-2302 | A40 M1 motor B+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-071 | 55GAD0-GM-2302:CR-CCC | 55GAD0-GM-2302 | A40 M1 motor B- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-072 | 55GAD0-MTE-2101:TE-CRC | 55GAD0-MTE-2101 | IOT structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-073 | 55GAD0-MTE-2102:TE-CRC | 55GAD0-MTE-2102 | IOT structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-074 | 55GAD0-MTE-2103:TE-CRC | 55GAD0-MTE-2103 | IOT structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-075 | 55GAD0-MTE-2104:TE-CRC | 55GAD0-MTE-2104 | IOT structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-076 | 55GAD0-MTE-2105:TE-CRC | 55GAD0-MTE-2105 | A50 assembly thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-077 | 55GAD0-MTE-2106:TE-CRC | 55GAD0-MTE-2106 | A50 assembly thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-078 | 55GAD0-MTE-2107:TE-CRC | 55GAD0-MTE-2107 | A50 assembly thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-079 | 55GAD0-MTE-2108:TE-CRC | 55GAD0-MTE-2108 | A50 assembly thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-080 | 55GAD0-MTE-2109:TE-CRC | 55GAD0-MTE-2109 | A50 assembly thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-081 | 55GAD0-MTE-2110:TE-CRC | 55GAD0-MTE-2110 | A50 assembly thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-082 | 55GAD0-MTE-2111:TE-CRC | 55GAD0-MTE-2111 | A50 assembly thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-083 | 55GAD0-MTE-2112:TE-CRC | 55GAD0-MTE-2112 | A50 assembly thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-084 | 55GAD0-MTE-2113:TE-CRC | 55GAD0-MTE-2113 | A50 assembly thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-085 | 55GAD0-MTE-2114:TE-CRC | 55GAD0-MTE-2114 | A50 assembly thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-086 | 55GAD0-MTE-2115:TE-CRC | 55GAD0-MTE-2115 | A50 assembly thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-087 | 55GAD0-MTE-2116:TE-CRC | 55GAD0-MTE-2116 | A50 assembly thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-088 | 55GAD0-MTE-2201:TE-CRC | 55GAD0-MTE-2201 | BOL structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-089 | 55GAD0-MTE-2202:TE-CRC | 55GAD0-MTE-2202 | BOL structure thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-090 | 55GAD0-MTE-2501:TE-CRC | 55GAD0-MTE-2501 | A60 M2 thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-091 | 55GAD0-MTE-2502:TE-CRC | 55GAD0-MTE-2502 | A60 M2 thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-092 | 55GAD0-MZH-2501:ZH-CRC | 55GAD0-MZH-2501 | A60 M2 limit switch high | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-093 | 55GAD0-MZL-2501:ZL-CRC | 55GAD0-MZL-2501 | A60 M2 limit switch low | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-094 | 55GAD0-MZH-2502:ZH-CRC | 55GAD0-MZH-2502 | A60 M2 limit switch high | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-095 | 55GAD0-MZL-2502:ZL-CRC | 55GAD0-MZL-2502 | A60 M2 limit switch low | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-096 | 55GAD0-GM-2501:CR-CCC | 55GAD0-GM-2501 | A60 M2 motor A+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-097 | 55GAD0-GM-2501:CR-CCC | 55GAD0-GM-2501 | A60 M2 motor A- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-098 | 55GAD0-GM-2501:CR-CCC | 55GAD0-GM-2501 | A60 M2 motor B+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-099 | 55GAD0-GM-2501:CR-CCC | 55GAD0-GM-2501 | A60 M2 motor B- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-100 | 55GAD0-GM-2502:CR-CCC | 55GAD0-GM-2502 | A60 M2 motor A+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-101 | 55GAD0-GM-2502:CR-CCC | 55GAD0-GM-2502 | A60 M2 motor A- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-102 | 55GAD0-GM-2502:CR-CCC | 55GAD0-GM-2502 | A60 M2 motor B+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-103 | 55GAD0-GM-2502:CR-CCC | 55GAD0-GM-2502 | A60 M2 motor B- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-104 | 55GAD0-MTE-2503:TE-CRC | 55GAD0-MTE-2503 | A60 M1 thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-105 | 55GAD0-MTE-2504:TE-CRC | 55GAD0-MTE-2504 | A60 M1 thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-106 | 55GAD0-MZH-2503:ZH-CRC | 55GAD0-MZH-2503 | A60 M1 limit switch high | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-107 | 55GAD0-MZL-2503:ZL-CRC | 55GAD0-MZL-2503 | A60 M1 limit switch low | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-108 | 55GAD0-MZH-2504:ZH-CRC | 55GAD0-MZH-2504 | A60 M1 limit switch high | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-109 | 55GAD0-MZL-2504:ZL-CRC | 55GAD0-MZL-2504 | A60 M1 limit switch low | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-110 | 55GAD0-GM-2503:CR-CCC | 55GAD0-GM-2503 | A60 M1 motor A+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-111 | 55GAD0-GM-2503:CR-CCC | 55GAD0-GM-2503 | A60 M1 motor A- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-112 | 55GAD0-GM-2503:CR-CCC | 55GAD0-GM-2503 | A60 M1 motor B+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-113 | 55GAD0-GM-2503:CR-CCC | 55GAD0-GM-2503 | A60 M1 motor B- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-114 | 55GAD0-GM-2504:CR-CCC | 55GAD0-GM-2504 | A60 M1 motor A+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-115 | 55GAD0-GM-2504:CR-CCC | 55GAD0-GM-2504 | A60 M1 motor A- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-116 | 55GAD0-GM-2504:CR-CCC | 55GAD0-GM-2504 | A60 M1 motor B+ | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-117 | 55GAD0-GM-2504:CR-CCC | 55GAD0-GM-2504 | A60 M1 motor B- | A | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-118 | 55GAD0-MZL-4301:ZL-CRC | 55GAD0-MZL-4301 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-119 | 55GAD0-MZH-4301:ZH-CRC | 55GAD0-MZH-4301 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-120 | 55GAD0-MZL-4302:ZL-CRC | 55GAD0-MZL-4302 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-121 | 55GAD0-MZH-4302:ZH-CRC | 55GAD0-MZH-4302 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-122 | 55GAD0-MZL-4303:ZL-CRC | 55GAD0-MZL-4303 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-123 | 55GAD0-MZH-4303:ZH-CRC | 55GAD0-MZH-4303 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-124 | 55GAD0-MZL-4304:ZL-CRC | 55GAD0-MZL-4304 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-125 | 55GAD0-MZH-4304:ZH-CRC | 55GAD0-MZH-4304 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-126 | 55GAD0-MZL-4305:ZL-CRC | 55GAD0-MZL-4305 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-127 | 55GAD0-MZH-4305:ZH-CRC | 55GAD0-MZH-4305 | Pneumatic shutter limit switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-128 | 55GAD0-MP-4302:JT-CRC | 55GAD0-MP-4302 | Pressure sensor at pneumatic shutter valves power | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-129 | 55GAD0-MP-4302:JT-CRC | 55GAD0-MP-4302 | Pressure sensor at pneumatic shutter valves output | A | O | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-130 | 55GAD0-MP-4301:JT-CRC | 55GAD0-MP-4301 | Pressure sensor at pneumatic shutter valves power | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-131 | 55GAD0-MP-4301:JT-CRC | 55GAD0-MP-4301 | Pressure sensor at pneumatic shutter valves output | A | O | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-132 | 55GAD0-PL-4401:YTRP-CCC | 55GAD0-PL-4401 | LO Level | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-133 | 55GAD0-PL-4401:CC-CCC | 55GAD0-PL-4401 | Relay 1 NO | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-134 | 55GAD0-PL-4401:CO-CCC | 55GAD0-PL-4401 | Relay 1 NC | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-135 | 55GAD0-PL-4401:YTRP-CCC | 55GAD0-PL-4401 | Relay 2 | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-136 | 55GAD0-PL-4401: YREM-CCC | 55GAD0-PL-4401 | Remote Start | A | I | P | 0 +10V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-137 | 55GAD0-PL-4401: YREM-CCC | 55GAD0-PL-4401 | Remote Set Point | A | I | P | 0 +10V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-138 | 55GAD0-PL-4401: YTRP-CCC | 55GAD0-PL-4401 | Lo Flow | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-139 | 55GAD0-PL-4401: YSTA-CCC | 55GAD0-PL-4401 | Pump on | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-140 | 55GAD0-PL-4401: TE-CCC | 55GAD0-PL-4401 | text out/ext | A | O | P | 0 +10 V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-141 | 55GAD0-PL-4402: YTRP-CCC | 55GAD0-PL-4402 | LO Level | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-142 | 55GAD0-PL-4402: CC-CCC | 55GAD0-PL-4402 | Relay 1 NO | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-143 | 55GAD0-PL-4402: CO-CCC | 55GAD0-PL-4402 | Relay 1 NC | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-144 | 55GAD0-PL-4402: YTRP-CCC | 55GAD0-PL-4402 | Relay 2 | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-145 | 55GAD0-PL-4402: YREM-CCC | 55GAD0-PL-4402 | Remote Start | A | I | P | 0 +10 V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-146 | 55GAD0-PL-4402: YREM-CCC | 55GAD0-PL-4402 | Remote Set Point | A | I | P | 0 +10 V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-147 | 55GAD0-PL-4402: YTRP-CCC | 55GAD0-PL-4402 | Lo Flow | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-148 | 55GAD0-PL-4402: YSTA-CCC | 55GAD0-PL-4402 | Pump on | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-149 | 55GAD0-PL-4402: TE-CCC | 55GAD0-PL-4402 | text out/ext | A | O | P | 0 +10 V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-150 | 55GAD0-ATG-4401: CO-CRC | 55GAD0-ATG-4401 | Shutter actuator ON/OFF Valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-151 | 55GAD0-ATG-4402: CO-CRC | 55GAD0-ATG-4402 | Stutter actuation ON/OFF Valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-152 | 55GAD0-ATG-4403: CO-CRC | 55GAD0-ATG-4403 | Shutter actuation ON/OFF Valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-153 | 55GAD0-ATG-4404: CO-CRC | 55GAD0-ATG-4404 | Shutter actuation ON/OFF Valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-154 | 55GAD0-ATG-4405: CO-CRC | 55GAD0-ATG-4405 | Shutter actuation ON/OFF Valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-155 | 55GAD0-MZS-3301: ZL-CRC | 55GAD0-MZS-3301 | filter wheel home switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-156 | 55GAD0-MZS-3302: ZL-CRC | 55GAD0-MZS-3302 | filter wheel home switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-157 | 55GAD0-MZS-3303: ZL-CRC | 55GAD0-MZS-3303 | filter wheel home switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-158 | 55GAD0-MZS-3304: ZL-CRC | 55GAD0-MZS-3304 | filter wheel home switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-159 | 55GAD0-MZS-3305: ZL-CRC | 55GAD0-MZS-3305 | filter wheel home switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-160 | 55GAD0-MZS-3306: ZL-CRC | 55GAD0-MZS-3306 | filter wheel home switch | D | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-161 | 55GAD0-CCD-3202: BTVT-CRC | 55GAD0-CCD-3202 | Camera Visible 1 Video signal transmit | E | I | P | 0 +10 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-162 | 55GAD0-CCD-3204: BTVT-CRC | 55GAD0-CCD-3204 | Camera Visible 2 video signal transmit | E | I | P | 0 +10 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-163 | 55GAD0-CCD-3201: BTVT-CRC | 55GAD0-CCD-3201 | Camera IR 1 Video signal transmit | E | I | P | 0 +10 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-164 | 55GAD0-CCD-3203: BTVT-CRC | 55GAD0-CCD-3203 | Camera IR 2 video signal transmit | E | I | P | 0 +10 V | 55GAD0-CU-7302 | unconfirmed
D1-N9-GAD0-SIG-165 | 55GAD0-GM-3202:CR-CCC | 55GAD0-GM-3202 | Linear stage motor for visible camera 1 A+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-166 | 55GAD0-GM-3202:CR-CCC | 55GAD0-GM-3202 | Linear stage motor for visible camera 1 A- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-167 | 55GAD0-GM-3202:CR-CCC | 55GAD0-GM-3202 | Linear stage motor for visible camera 1 B+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-168 | 55GAD0-GM-3202:CR-CCC | 55GAD0-GM-3202 | Linear stage motor for visible camera 1 B- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-169 | 55GAD0-GM-3204:CR-CCC | 55GAD0-GM-3204 | Linear stage motor for visible camera 2 A+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-170 | 55GAD0-GM-3204:CR-CCC | 55GAD0-GM-3204 | Linear stage motor for visible camera 2 A- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-171 | 55GAD0-GM-3204:CR-CCC | 55GAD0-GM-3204 | Linear stage motor for visible camera 2 B+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-172 | 55GAD0-GM-3204:CR-CCC | 55GAD0-GM-3204 | Linear stage motor for visible camera 2 B- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-173 | 55GAD0-GM-3301:CR-CCC | 55GAD0-GM-3301 | Filter wheel motor 1 A+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-174 | 55GAD0-GM-3301:CR-CCC | 55GAD0-GM-3301 | Filter wheel motor 1 A- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-175 | 55GAD0-GM-3301:CR-CCC | 55GAD0-GM-3301 | Filter wheel motor 1 B+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-176 | 55GAD0-GM-3301:CR-CCC | 55GAD0-GM-3301 | Filter wheel motor 1 B- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-177 | 55GAD0-GM-3302:CR-CCC | 55GAD0-GM-3302 | Filter wheel motor 2 A+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-178 | 55GAD0-GM-3302:CR-CCC | 55GAD0-GM-3302 | Filter wheel motor 2 A- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-179 | 55GAD0-GM-3302:CR-CCC | 55GAD0-GM-3302 | Filter wheel motor 2 B+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-180 | 55GAD0-GM-3302:CR-CCC | 55GAD0-GM-3302 | Filter wheel motor 2 B- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-181 | 55GAD0-GM-3303:CR-CCC | 55GAD0-GM-3303 | Filter wheel motor 3 A+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-182 | 55GAD0-GM-3303:CR-CCC | 55GAD0-GM-3303 | Filter wheel motor 3 A- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-183 | 55GAD0-GM-3303:CR-CCC | 55GAD0-GM-3303 | Filter wheel motor 3 B+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-184 | 55GAD0-GM-3303:CR-CCC | 55GAD0-GM-3303 | Filter wheel motor 3 B- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-185 | 55GAD0-GM-3304:CR-CCC | 55GAD0-GM-3304 | Filter wheel motor 4 A+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-186 | 55GAD0-GM-3304:CR-CCC | 55GAD0-GM-3304 | Filter wheel motor 4 A- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-187 | 55GAD0-GM-3304:CR-CCC | 55GAD0-GM-3304 | Filter wheel motor 4 B+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-188 | 55GAD0-GM-3304:CR-CCC | 55GAD0-GM-3304 | Filter wheel motor 4 B- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-189 | 55GAD0-GM-3305:CR-CCC | 55GAD0-GM-3305 | Filter wheel motor 5 A+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-190 | 55GAD0-GM-3305:CR-CCC | 55GAD0-GM-3305 | Filter wheel motor 5 A- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-191 | 55GAD0-GM-3305:CR-CCC | 55GAD0-GM-3305 | Filter wheel motor 5 B+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-192 | 55GAD0-GM-3305:CR-CCC | 55GAD0-GM-3305 | Filter wheel motor 5 B- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-193 | 55GAD0-GM-3306:CR-CCC | 55GAD0-GM-3306 | Filter wheel motor 6 A+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-194 | 55GAD0-GM-3306:CR-CCC | 55GAD0-GM-3306 | Filter wheel motor 6 A- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-195 | 55GAD0-GM-3306:CR-CCC | 55GAD0-GM-3306 | Filter wheel motor 6 B+ | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-196 | 55GAD0-GM-3306:CR-CCC | 55GAD0-GM-3306 | Filter wheel motor 6 B- | D | O | P | 0 +24V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-197 | 55GAD0-CSO-3101:CON-CCC | 55GAD0-CSO-3101 | Blackbody source command on | D | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-198 | 55GAD0-CSO-3101:COFF-CCC | 55GAD0-CSO-3101 | Blackbody source command off | D | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-199 | 55GAD0-CSO-3101:JT-CRC | 55GAD0-CSO-3101 | blackbody source power | A | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-200 | 55GAD0-CSO-3101:CREF-CCC | 55GAD0-CSO-3101 | Blackbody source set point | A | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-201 | 55GAD0-MTE-3105:TE-CRC | 55GAD0-MTE-3105 | blackbody source temperature from thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-202 | 55GAD0-CSO-3102:JT-CRC | 55GAD0-CSO-3102 | Integrated spherere power | A | I | P | 0 +10 V | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-203 | 55GAD0-MTE-3201:TE-CRC | 55GAD0-MTE-3201 | Camera optical bench thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-204 | 55GAD0-MTE-3202:TE-CRC | 55GAD0-MTE-3202 | Camera optical bench thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-205 | 55GAD0-MTE-3203:TE-CRC | 55GAD0-MTE-3203 | Camera optical bench thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-206 | 55GAD0-MTE-3204:TE-CRC | 55GAD0-MTE-3204 | Camera optical bench thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-207 | 55GAD0-MTE-3205:TE-CRC | 55GAD0-MTE-3205 | Camera optical bench thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-208 | 55GAD0-MTE-3206:TE-CRC | 55GAD0-MTE-3206 | Camera optical bench thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-209 | 55GAD0-MTE-3207:TE-CRC | 55GAD0-MTE-3207 | Camera optical bench thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-210 | 55GAD0-MTE-3208:TE-CRC | 55GAD0-MTE-3208 | Camera optical bench thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-211 | 55GAD0-MTE-3209:TE-CRC | 55GAD0-MTE-3209 | Camera optical bench thermocouple | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-212 | 55GAD0-MTE-3210:TE-CRC | 55GAD0-MTE-3210 | Camera optical bench thermocouple | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-213 | 55GAD0-RCK-3100:JT-CCC | 55GAD0-RCK-3100 | RF matching box 1 power | A | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-214 | 55GAD0-RCK-3100:JREF-CCC | 55GAD0-RCK-3100 | RF matching box 1 power from RF generator | A | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-215 | 55GAD0-RCK-3100: JT-CCC | 55GAD0-RCK-3100 | RF matching box 1 power to mirror (forward) | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-216 | 55GAD0-RCK-3100: JT-CCC | 55GAD0-RCK-3100 | RF matching box 1 reverse power from mirror | D | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-217 | 55GAD0-RCK-3200: JT-CCC | 55GAD0-RCK-3200 | RF matching box 2 power | A | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-218 | 55GAD0-RCK-3200: JREF-CCC | 55GAD0-RCK-3200 | RF matching box 2 power from RF generator | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-219 | 55GAD0-RCK-3200: JT-CCC | 55GAD0-RCK-3200 | RF matching box 2 power to mirror (forward) | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-220 | 55GAD0-RCK-3200: JT-CCC | 55GAD0-RCK-3200 | RF matching box 2 reverse power from mirror | D | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-221 | 55GAD0-MPE-7073: JT-CRC | 55GAD0-MPE-7073 | Pressure sensor chilled water | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-222 | 55GAD0-MPE-7073: JT-CRC | 55GAD0-MPE-7073 | Pressure sensor chilled water | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-223 | 55GAD0-MTE-7373: TE-CRC | 55GAD0-MTE-7373 | Thermocpuples chilled water | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-224 | 55GAD0-MPE-7074: JT-CRC | 55GAD0-MPE-7074 | Pressure sensor chilled water | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-225 | 55GAD0-MPE-7074: JT-CRC | 55GAD0-MPE-7074 | Pressure sensor chilled water | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-226 | 55GAD0-MTE-7374: TE-CRC | 55GAD0-MTE-7374 | Thermocpuples chilled water | A | I | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-227 | 55GAD0-MFE-7074: JT-CRC | 55GAD0-MFE-7074 | mass flow sensor chilled water | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-228 | 55GAD0-MFE-7074: JT-CRC | 55GAD0-MFE-7074 | Mass flow sensor chilled water | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-229 | 55GAD0-ATC-1008: CO-CRC | 55GAD0-ATC-1008 | Shutter actuation ON/OFF Valve | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-230 | 55GAD0-MPE-7071: JT-CRC | 55GAD0-MPE-7071 | Pressure sensor chilled water | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-231 | 55GAD0-MPE-7071: JT-CRC | 55GAD0-MPE-7071 | Pressure sensor chilled water | A | O | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-232 | 55GAD0-MTE-7371: TE-CRC | 55GAD0-MTE-7371 | Thermocpuples chilled water | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-233 | 55GAD0-MPE-7072: JT-CRC | 55GAD0-MPE-7072 | Pressure sensor chilled water | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-234 | 55GAD0-MPE-7072: JT-CRC | 55GAD0-MPE-7072 | Pressure sensor chilled water | A | O | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-235 | 55GAD0-MTE-7372: TE-CRC | 55GAD0-MTE-7372 | Thermocpuples chilled water | A | O | P | T/C Type N | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-236 | 55GAD0-MFE-7073: JT-CRC | 55GAD0-MFE-7073 | Pressure sensor chilled water | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-237 | 55GAD0-MFE-7073: JT-CRC | 55GAD0-MFE-7073 | Pressure sensor chilled water | A | O | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-238 | 55GAD0-ATC-1007: CO-CRC | 55GAD0-ATC-1007 | Shutter Actuation ON/OFF Valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-239 | 55GAD0-PSU-9211: CON-CCC | 55GAD0-PSU-9211 | RF generator 1 command on | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-240 | 55GAD0-PSU-9211: COF-CCC | 55GAD0-PSU-9211 | RF generator 1 command off | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-241 | 55GAD0-PSU-9211: CREF-CCC | 55GAD0-PSU-9211 | RF generator 1 RF power set point | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-242 | 55GAD0-PSU-9211: SREF-CCC | 55GAD0-PSU-9211 | RF generator 1 forward power | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-243 | 56GAD0-PSU-9211: SREF-CCC | 55GAD0-PSU-9211 | RF generator 1 reflected power | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-243 | 56GAD0-PSU-9211: SREF-CCC | 55GAD0-PSU-9211 | RF generator 1 tune cap position | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-244 | 57GAD0-PSU-9211: SREF-CCC | 55GAD0-PSU-9211 | RF generator 1 load cap position | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-245 | 58GAD0-PSU-9211: SREF-CCC | 55GAD0-PSU-9211 | RF generator 1 move tune cap position | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-246 | 59GAD0-PSU-9211: SREF-CCC | 55GAD0-PSU-9211 | RF generator 1 move load cap position | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-247 | 60GAD0-PSU-9211: SREF-CCC | 55GAD0-PSU-9211 | RF generator 1 phase | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-248 | 61GAD0-PSU-9211: SREF-CCC | 55GAD0-PSU-9211 | RF generator 1 RF on/off | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-249 | 62GAD0-PSU-9211: SREF-CCC | 55GAD0-PSU-9211 | RF generator 1 sync bus | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-243 | 55GAD0-PSU-9211: JT-CRC | 55GAD0-PSU-9211 | RF generator 1 matching mode | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-244 | 55GAD0-PSU-9214: CON-CCC | 55GAD0-PSU-9214 | RF generator 2 command on | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-245 | 55GAD0-PSU-9214: COF-CCC | 55GAD0-PSU-9214 | RF generator 2 command off | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-246 | 55GAD0-PSU-9214: CREF-CCC | 55GAD0-PSU-9214 | RF generator 2 RF power set point | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-247 | 55GAD0-PSU-9214: SREF-CCC | 55GAD0-PSU-9214 | RF generator 2 forward power | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-248 | 55GAD0-PSU-9214: JT-CRC | 55GAD0-PSU-9214 | RF generator 2 reflected power | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-249 | 56GAD0-PSU-9214: JT-CRC | 55GAD0-PSU-9214 | RF generator 2 tune cap position | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-250 | 57GAD0-PSU-9214: JT-CRC | 55GAD0-PSU-9214 | RF generator 2 load cap position | E | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-251 | 58GAD0-PSU-9214: JT-CRC | 55GAD0-PSU-9214 | RF generator 2 move tune cap position | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-252 | 59GAD0-PSU-9214: JT-CRC | 55GAD0-PSU-9214 | RF generator 2 move load cap position | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-253 | 60GAD0-PSU-9214: JT-CRC | 55GAD0-PSU-9214 | RF generator 2 phase | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-254 | 61GAD0-PSU-9214: JT-CRC | 55GAD0-PSU-9214 | RF generator 2 RF on/off | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-255 | 62GAD0-PSU-9214: JT-CRC | 55GAD0-PSU-9214 | RF generator 2 sync bus | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-256 | 63GAD0-PSU-9214: JT-CRC | 55GAD0-PSU-9214 | RF generator 2 matching mode | E | O | P | custom | 55GAD0-CU-7301 | unconfirmed
| TBD | TBD | Stepper motor controlled by PLC that will control load cap position | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
| TBD | TBD | Stepper motor controlled by PLC that will control tune cap position | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
| TBD | TBD | High limit switch for load cap stepper motor | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
| TBD | TBD | Low limit switch for load cap stepper motor | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
| TBD | TBD | High limit switch for tune cap stepper motor | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
| TBD | TBD | Low limit switch for tune cap stepper motor | D | O | P | custom | 55GAD0-CU-7301 | unconfirmed
| TBD | TBD | VSWR meter for measuring reflected power | A | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-249 | 55GAD0-PSU-9001: JT-CRC | 55GAD0-PSU-9001 | DCPS1 power | D | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-250 | 55GAD0-PSU-9002: JT-CRC | 55GAD0-PSU-9002 | DCPS2 power | D | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-251 | 55GAD0-PSU-9003: JT-CRC | 55GAD0-PSU-9003 | DCPS3 power | A | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-252 | 55GAD0-PSU-9004: JT-CRC | 55GAD0-PSU-9004 | DCPS4 power | A | I | P | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-253 | 55GAD0-SCI-9101: JT-CRC | 55GAD0-SCI-9101 | filament signal conditioning | custom | custom | custom | custom | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-254 | 55GAD0-ATC-1009: CO-CRC | 55GAD0-ATC-1009 | Shutter Actuation ON/OFF Valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-255 | 55GAD0-ATC-1010: CO-CRC | 55GAD0-ATC-1010 | Shutter Actuation ON/OFF Valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-256 | 55GAD0-MZL-0301:ZL-CRC | 55GAD0-MZL-0301 | Low limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-257 | 55GAD0-MZH-0301:ZH-CRC | 55GAD0-MZH-0301 | High limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-258 | 55GAD0-MZL-0315:ZL-CRC | 55GAD0-MZL-0315 | Low limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-259 | 55GAD0-MZH-0315:ZH-CRC | 55GAD0-MZH-0315 | High limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-260 | 55GAD0-MZL-0317:ZL-CRC | 55GAD0-MZL-0317 | Low limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-261 | 55GAD0-MZH-0317:ZH-CRC | 55GAD0-MZH-0317 | High limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-262 | 55GAD0-MZL-0319:ZL-CRC | 55GAD0-MZL-0319 | Low limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-263 | 55GAD0-MZH-0319:ZH-CRC | 55GAD0-MZH-0319 | High limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-264 | 55GAD0-MZL-0321:ZL-CRC | 55GAD0-MZL-0321 | Low limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-265 | 55GAD0-MZH-0321:ZH-CRC | 55GAD0-MZH-0321 | High limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-266 | 55GAD0-MZL-0322:ZL-CRC | 55GAD0-MZL-0322 | Low limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-267 | 55GAD0-MZH-0322:ZH-CRC | 55GAD0-MZH-0322 | High limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-268 | 55GAD0-MZL-0323:ZL-CRC | 55GAD0-MZL-0323 | Low limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-269 | 55GAD0-MZH-0323:ZH-CRC | 55GAD0-MZH-0323 | Low limit switch for pneumatic valve | A | I | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-270 | 55GAD0-MP-0001:JT-CRC | 55GAD0-MP-0001 | Pressure transmitter | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-271 | 55GAD0-MP-0002:JT-CRC | 55GAD0-MP-0002 | Pressure transmitter | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-272 | 55GAD0-MP-0004:JT-CRC | 55GAD0-MP-0004 | Pressure transmitter | A | I | P | PT 100 | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-273 | 55GAD0-ATG-0301:CO-CRC | 55GAD0-ATG-0301 | Air line actuator | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-274 | 55GAD0-ATG-0315:CO-CRC | 55GAD0-ATG-0315 | Air line actuator | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-275 | 55GAD0-ATG-0317:CO-CRC | 55GAD0-ATG-0317 | Air line actuator | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-276 | 55GAD0-ATG-0319:CO-CRC | 55GAD0-ATG-0319 | Air line actuator | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-277 | 55GAD0-ATG-0321:CO-CRC | 55GAD0-ATG-0321 | Air line actuator | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-278 | 55GAD0-ATC-0322:CO-CRC | 55GAD0-ATC-0322 | Air line actuator | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed
D1-N9-GAD0-SIG-279 | 55GAD0-ATC-0010:CO-CRC | 55GAD0-ATC-0010 | Air line actuator | A | O | P | 24 V DC | 55GAD0-CU-7301 | unconfirmed

## Info
| ID Format | Example
Signal | CBS1-CBS2-CBS3-SIG-nnn | D1-IG-B3D0-SIG-001 | Range | Logic | Definition | Signal type | Definition | Direction |  | Location
Componet | CBS1-CBS2-CBS3-COMP-nnn | D1-IG-B3D0-COMP-001 | 0 +10 V | P | P-Positive | D | Digital | I-Input | I | 11-B1-01
|  |  | -10 +10 V | N | N-Negative | A | Analog | O-Output | O | 11-B1-02E
| Naming Conventions | Example | -5 +5 V |  |  | E | Ethernet |  |  | 11-B1-02N
Signal | Component Identifier:Signal Identifier PPPPPP-TTT-NNNN:AAAA[RRRR]-SSS | 55UI00-MT-0001:TT-CRC | 4 20 mA | [6 empty] | 11-B1-02S
Component | PPPPPP-TTT-NNNN | 55UI00-MT-0001 | PT 100 | [6 empty] | 11-B1-02W
|  |  | T/C Type K | [6 empty] | 11-B1-ANW
PPPPPP | The PBS Identifier |  | T/C Type N | [6 empty] | 11-B1-ASW
TTT | Function Category Designator |  | 24 V DC | [6 empty] | 11-B1-C01
NNNN | The Sequential Number |  | Fieldbus | [6 empty] | 11-B1-C02
AAAA | The first part AAAA identifies the sensor/actuator class using the ISA-5.1-1984 (R1992) standard for instrumentation symbols and identification |  | RS 485 | Direction | Definition |  |  |  |  | 11-B1-C03
RRRR | The second part RRRR is optional and used to identify several sensors/actuators of the same class within the component. |  | 0 +3.3 V | I | [5 empty] | 11-B1-C04
SSS | The third part SSS is used to identify the signal type |  | 0 20 mA | O | [5 empty] | 11-B1-C05
|  |  | Custom | I/O | [5 empty] | 11-B1-C06
|  |  | -1 +1 V | [6 empty] | 11-B1-C07
|  |  | 0 +5 V | [6 empty] | 11-B1-C08
|  |  | LVDS | [6 empty] | 11-B1-C09
|  |  | RS 422 | [6 empty] | 11-B1-C10
|  |  | RS 232 | [6 empty] | 11-B1-C11
|  |  | PECL | [6 empty] | 11-B1-C12
|  |  | 12 V DC | [6 empty] | 11-B1-C13
|  |  | 15 V DC | [6 empty] | 11-B1-C14
|  |  | -12 V DC | [6 empty] | 11-B1-C15
|  |  | 5 V DC | [6 empty] | 11-B1-C16
|  |  | -5 V DC | [6 empty] | 11-B1-C17
|  |  | CML | [6 empty] | 11-B1-C18
|  |  | 0 +24V | [6 empty] | 11-B1-LFT
11-B1-PNW
11-B1-PSW
11-B1-V01
11-B1-V02
11-B1-V03
11-B1-V04
11-B1-V05
11-B1-V06
11-B1-V07
11-B1-V08
11-B1-V09
11-B1-V10
11-B1-V11
11-B1-V12
11-B1-V13
11-B1-V14
11-B1-V15
11-B1-V16
11-B1-V17
11-B1-V18
11-B1-VNE
11-B1-VNW
11-B1-VSE
11-B1-VSE1
11-B1-VSE2
11-B1-VSW
11-B2-01
11-B2-02E
11-B2-02N
11-B2-02S
11-B2-02W
11-B2-04NE
11-B2-04SE
11-B2-05NE
11-B2-05NW
11-B2-05SE
11-B2-ANW
11-B2-ASW
11-B2-LFT
11-B2-PIT
11-B2-SU1
11-B2-SU2
11-B2-SU3
11-B2-SU4
11-B2-SU5
11-B2-VNE
11-B2-VNW
11-B2-VSE
11-B2-VSE1
11-B2-VSE2
11-B2-VSW
11-B2M-01E
11-B2M-01N
11-B2M-01S
11-B2M-01W
11-B2M-SN
11-B2M-SS
11-B2M-SW
11-L1-02E
11-L1-02S
11-L1-02W
11-L1-04NE
11-L1-05NW
11-L1-A
11-L1-ANB
11-L1-ANW
11-L1-ASW
11-L1-C
11-L1-C01
11-L1-C02
11-L1-C03
11-L1-C08
11-L1-C09
11-L1-C10
11-L1-C11
11-L1-C12
11-L1-C13
11-L1-C14
11-L1-C15
11-L1-C16
11-L1-C17
11-L1-C18
11-L1-CNB
11-L1-LFT
11-L1-PNW
11-L1-PSW
11-L1-V01
11-L1-V02
11-L1-V03
11-L1-V08
11-L1-V09
11-L1-V10
11-L1-V11
11-L1-V12
11-L1-V13
11-L1-V14
11-L1-V15
11-L1-V16
11-L1-V17
11-L1-V18
11-L1-VNE
11-L1-VNW
11-L1-VSE
11-L1-VSE1
11-L1-VSE2
11-L1-VSW
11-L2-01
11-L2-02E
11-L2-02S
11-L2-02W
11-L2-04SW
11-L2-05SE
11-L2-ANW
11-L2-ASW
11-L2-C01
11-L2-C02
11-L2-C03
11-L2-C08
11-L2-C09
11-L2-C10
11-L2-C11
11-L2-C12
11-L2-C13
11-L2-C14
11-L2-C15
11-L2-C16
11-L2-C17
11-L2-C18
11-L2-LFT
11-L2-PNW
11-L2-PSW
11-L2-V01
11-L2-V02
11-L2-V03
11-L2-V08
11-L2-V09
11-L2-V10
11-L2-V11
11-L2-V12
11-L2-V13
11-L2-V14
11-L2-V15
11-L2-V16
11-L2-V17
11-L2-V18
11-L2-VNE
11-L2-VNW
11-L2-VSE
11-L2-VSE1
11-L2-VSE2
11-L2-VSW
11-L3-01
11-L3-02E
11-L3-02S
11-L3-02W
11-L3-03E
11-L3-03N
11-L3-03S
11-L3-03W
11-L3-04NE
11-L3-04SW
11-L3-05
11-L3-ANW
11-L3-ASW
11-L3-LFT
11-L3-PNW
11-L3-PSW
11-L3-V01
11-L3-V02
11-L3-V03
11-L3-V08
11-L3-V09
11-L3-V10
11-L3-V11
11-L3-V12
11-L3-V13
11-L3-V14
11-L3-V15
11-L3-V16
11-L3-V17
11-L3-V18
11-L3-VNE
11-L3-VNW
11-L3-VSE
11-L3-VSE1
11-L3-VSE2
11-L3-VSW
11-L4-01N
11-L4-01S
11-L4-02
11-L4-04
11-L4-LFT
11-L4-VNE
11-L4-VNW
11-L4-VSE
11-L4-VSE1
11-L4-VSE2
11-L4-VSW
11-L5-01
11-L5-02
11-L5-04N
11-L5-04S
11-L5-05N
11-L5-05S
11-L5-ANW
11-L5-ASW
11-L5-VNW
11-L5-VSW
11-OUT-NORTH
11-R1-01E
11-R1-01S
11-R1-01W
11-R1-02
11-R1-03
11-R1-04A
11-R1-04B
11-R1-05E
11-R1-A1
11-R1-VSWA
11-R1-VSWB
11-R1-VSWC
11-RP-11A
11-RP-11B
11-RP-8A
11-RP-8B
14-B1-01
14-B1-02
14-B1-02_TG
14-B1-03
14-B1-04
14-B1-05
14-B1-05A
14-B1-06
14-B1-06A
14-B1-07
14-B1-07A
14-B1-08
14-B1-09
14-B1-10
14-B1-11
14-B1-12
14-B1-13
14-B1-15
14-B1-20
14-B1-21
14-B1-22
14-B1-22A
14-B1-23
14-B1-24
14-B1-25
14-B1-26
14-B1-27
14-B1-28
14-B1-28A
14-B1-29
14-B1-A1
14-B1-A2
14-B1-A3
14-B1-A4
14-B1-A5
14-B1-L1
14-B1-L2
14-B1-L3
14-B1-LFT
14-B1-S1
14-B1-S2
14-B1-S3
14-B1-TG1
14-B1-TG2
14-B1-TG3
14-B1-TG4
14-B1-V1
14-B1-V2
14-B1-V3
14-B1-V4
14-B1-V5
14-B1-V6
14-B2-01
14-B2-02
14-B2-02_TG
14-B2-03
14-B2-04
14-B2-05
14-B2-06
14-B2-07
14-B2-08
14-B2-09
14-B2-10
14-B2-11
14-B2-12
14-B2-13
14-B2-15
14-B2-20
14-B2-21
14-B2-22
14-B2-23
14-B2-24
14-B2-25
14-B2-A1
14-B2-A2
14-B2-A3
14-B2-A4
14-B2-A5
14-B2-F1
14-B2-F2
14-B2-F3
14-B2-F4
14-B2-L1
14-B2-L2
14-B2-L3
14-B2-LFT
14-B2-S1
14-B2-S2
14-B2-S3
14-B2-SU1
14-B2-TG1
14-B2-TG2
14-B2-TG3
14-B2-TG4
14-B2-V1
14-B2-V2
14-B2-V3
14-B2-V4
14-B2-V5
14-B2-V6
14-L1-01
14-L1-02
14-L1-02_TG
14-L1-03
14-L1-04
14-L1-05
14-L1-05A
14-L1-06
14-L1-07
14-L1-07A
14-L1-08
14-L1-09
14-L1-10
14-L1-11
14-L1-12
14-L1-13
14-L1-14
14-L1-15
14-L1-20
14-L1-21
14-L1-22
14-L1-23
14-L1-23A
14-L1-23B
14-L1-23C
14-L1-24
14-L1-A1
14-L1-A2
14-L1-A3
14-L1-A4
14-L1-A5
14-L1-F1
14-L1-F2
14-L1-L1
14-L1-L2
14-L1-L3
14-L1-LFT
14-L1-S1
14-L1-S2
14-L1-S3
14-L1-TG1
14-L1-TG2
14-L1-TG3
14-L1-TG4
14-L1-V1
14-L1-V2
14-L1-V3
14-L1-V4
14-L1-V5
14-L1-V6
14-L2-01
14-L2-02
14-L2-02_TG
14-L2-03
14-L2-04
14-L2-05
14-L2-05A
14-L2-06
14-L2-06A
14-L2-07
14-L2-08
14-L2-09
14-L2-10
14-L2-11
14-L2-12
14-L2-13
14-L2-15
14-L2-20
14-L2-21
14-L2-22
14-L2-23
14-L2-24
14-L2-25
14-L2-A1
14-L2-A2
14-L2-A3
14-L2-A4
14-L2-A5
14-L2-L1
14-L2-L2
14-L2-L3
14-L2-LFT
14-L2-S1
14-L2-S2
14-L2-S3
14-L2-TG1
14-L2-TG2
14-L2-TG3
14-L2-TG4
14-L2-V1
14-L2-V2
14-L2-V3
14-L2-V4
14-L2-V5
14-L2-V6
14-L3-01
14-L3-02
14-L3-02_TG
14-L3-03
14-L3-04
14-L3-05
14-L3-05A
14-L3-06
14-L3-06A
14-L3-07
14-L3-08
14-L3-09
14-L3-10
14-L3-11
14-L3-12
14-L3-13
14-L3-15
14-L3-20
14-L3-21
14-L3-22
14-L3-23
14-L3-A1
14-L3-A2
14-L3-A3
14-L3-A4
14-L3-A5
14-L3-F1
14-L3-L1
14-L3-L2
14-L3-L3
14-L3-LFT
14-L3-S1
14-L3-S2
14-L3-S3
14-L3-TG1
14-L3-TG2
14-L3-TG3
14-L3-TG4
14-L3-V1
14-L3-V2
14-L3-V3
14-L3-V4
14-L3-V5
14-L3-V6
14-L4-01
14-L4-02
14-L4-03
14-L4-03_TG
14-L4-04
14-L4-07
14-L4-07_TG
14-L4-08
14-L4-09
14-L4-10
14-L4-11
14-L4-12
14-L4-13
14-L4-14
14-L4-20
14-L4-21
14-L4-22
14-L4-23
14-L4-24
14-L4-A1
14-L4-A2
14-L4-A3
14-L4-A4
14-L4-A5
14-L4-A6
14-L4-A7
14-L4-L1
14-L4-L2
14-L4-L3
14-L4-LFT
14-L4-S1
14-L4-S2
14-L4-S3
14-L4-TG1
14-L4-TG2
14-L4-V1
14-L4-V2
14-L4-V3
14-L4-V5
14-L4-V6
14-L5-01
14-L5-02
14-L5-02_TG
14-L5-03
14-L5-03A
14-L5-04
14-L5-05
14-L5-05A
14-L5-05B
14-L5-06
14-L5-07
14-L5-08
14-L5-09
14-L5-10
14-L5-11
14-L5-12
14-L5-15
14-L5-20
14-L5-21
14-L5-21A
14-L5-22
14-L5-23
14-L5-A1
14-L5-A2
14-L5-A3
14-L5-A5
14-L5-A6
14-L5-A7
14-L5-L1
14-L5-L2
14-L5-L3
14-L5-LFT
14-L5-S1
14-L5-S2
14-L5-S3
14-L5-TG1
14-L5-TG2
14-L5-TG3
14-L5-TG4
14-L5-V1
14-L5-V2
14-L5-V3
14-L5-V5
14-L5-V6
14-OUT-EAST
14-OUT-NORTH
14-OUT-SOUTH
14-R1-01
14-R1-02
14-R1-03
14-R1-04
14-R1-05
14-R1-A1
14-R1-A2
14-R1-A3
14-R1-A4
14-R1-L1
14-R1-LFT
14-R1-S1
14-R1-S2
14-R1-S3
14-R1-V1
14-R1-V2
14-R1-V3
14-R1-V5
14-R2-L1
14-R2-S1
74-B1-01
74-B1-02
74-B1-03
74-B1-04
74-B1-07
74-B1-08
74-B1-09
74-B1-10
74-B1-11
74-B1-12
74-B1-13
74-B1-14
74-B1-15
74-B1-16
74-B1-17
74-B1-18
74-B1-20
74-B1-21
74-B1-22
74-B1-24
74-B1-25
74-B1-26
74-B1-27
74-B1-28
74-B1-29
74-B1-ANW
74-B1-ASW
74-B1-LFT
74-B1-LN1
74-B1-LN2
74-B1-LS1
74-B1-LS2
74-B1-SN1
74-B1-SN2
74-B1-SS1
74-B1-SS2
74-B1-VN1
74-B1-VN2
74-B1-VN3
74-B1-VS1
74-B1-VS2
74-B1-VS3
74-B1-VS4
74-B1-VW1
74-B1-VW2
74-B1-VW3
74-B1-VW4
74-B1-VW5
74-B2-01
74-B2-02
74-B2-03
74-B2-04
74-B2-06
74-B2-07
74-B2-08
74-B2-10
74-B2-11
74-B2-12
74-B2-24
74-B2-25
74-B2-26
74-B2-27
74-B2-28
74-B2-ANW
74-B2-ASW
74-B2-LFT
74-B2-LN1
74-B2-LN2
74-B2-LS1
74-B2-LS2
74-B2-SN1
74-B2-SN2
74-B2-SS1
74-B2-SS2
74-B2-VN1
74-B2-VN2
74-B2-VN3
74-B2-VS1
74-B2-VS2
74-B2-VS3
74-B2-VS4
74-B2-VW1
74-B2-VW2
74-B2-VW3
74-B2-VW4
74-B2-VW5
74-L1-01
74-L1-02
74-L1-03
74-L1-04
74-L1-05
74-L1-06
74-L1-07
74-L1-08
74-L1-09
74-L1-10
74-L1-11
74-L1-12
74-L1-13
74-L1-14
74-L1-15
74-L1-16
74-L1-17
74-L1-18
74-L1-19
74-L1-20
74-L1-21
74-L1-22
74-L1-23
74-L1-24
74-L1-25
74-L1-28
74-L1-ANW
74-L1-ASW
74-L1-LFT
74-L1-LN1
74-L1-LN2
74-L1-LS1
74-L1-LS2
74-L1-SN1
74-L1-SN2
74-L1-SS1
74-L1-SS2
74-L1-VN1
74-L1-VN2
74-L1-VN3
74-L1-VS1
74-L1-VS2
74-L1-VS3
74-L1-VS4
74-L1-VW1
74-L1-VW2
74-L1-VW3
74-L1-VW4
74-L1-VW5
74-L2-01
74-L2-02
74-L2-03
74-L2-04
74-L2-05
74-L2-06
74-L2-07
74-L2-08
74-L2-09
74-L2-10
74-L2-11
74-L2-12
74-L2-13
74-L2-14
74-L2-15
74-L2-16
74-L2-17
74-L2-18
74-L2-19
74-L2-20
74-L2-21
74-L2-22
74-L2-23
74-L2-24
74-L2-25
74-L2-26
74-L2-27
74-L2-30
74-L2-32
74-L2-ANW
74-L2-ASW
74-L2-LFT
74-L2-LN1
74-L2-LN2
74-L2-LS1
74-L2-LS2
74-L2-SN1
74-L2-SN2
74-L2-SS1
74-L2-SS2
74-L2-VN1
74-L2-VN2
74-L2-VN3
74-L2-VS1
74-L2-VS2
74-L2-VS3
74-L2-VS4
74-L2-VW1
74-L2-VW2
74-L2-VW3
74-L2-VW4
74-L2-VW5
74-L3-01
74-L3-02
74-L3-03
74-L3-04
74-L3-05
74-L3-06
74-L3-07
74-L3-08
74-L3-09
74-L3-10
74-L3-11
74-L3-24
74-L3-25
74-L3-26
74-L3-27
74-L3-28
74-L3-ANW
74-L3-ASW
74-L3-LFT
74-L3-LN1
74-L3-LN2
74-L3-LS1
74-L3-LS2
74-L3-SN1
74-L3-SN2
74-L3-SS1
74-L3-SS2
74-L3-VN1
74-L3-VN2
74-L3-VN3
74-L3-VS1
74-L3-VS2
74-L3-VS3
74-L3-VS4
74-L3-VW1
74-L3-VW2
74-L3-VW3
74-L3-VW4
74-L3-VW5
74-L4-03
74-L4-25
74-L4-26
74-L4-27
74-L4-28
74-L4-29
74-L4-AN1
74-L4-AN2
74-L4-LFT
74-L4-LN1
74-L4-LS1
74-L4-LS2
74-L4-SN1
74-L4-SN2
74-L4-SS1
74-L4-SS2
74-L4-VS4
74-L5-02
74-L5-03
74-L5-AN1
74-L5-ANW
74-L5-LN1
74-L5-LS1
74-L5-SN1
74-L5-SS1
74-OUT-NORTH
74-OUT-SOUTH
74-OUT-WEST
74-R1-01
74-R1-LFT
74-R1-SN2
CST-S07-UPR_14
74-R1-SS2